## Channu
Feeder Name | Account No. | Connected HP / Sanctioned Demand | Type of Pump | Existing Pump Set Measured Parameters |  |  |  | Energy Efficient Pump Sets Parameters
|  |  |  | Total Head (m) | Flow (l/s) | Power (kW) | Efficiency (%) | Head (m) | Flow (l/s) | Efficiency (%)
Channu | 3376 | 5 | Monoblock | 6.5117 | 21.4797 | 4.6617 | 29.4337 | 7 | 22.5 | 56
Channu | 3448 | 5 | Monoblock | 3.083 | 26.7857 | 4.4155 | 18.3474 | 5 | 26 | 46
Channu | 735 | 5 | Monoblock | 3.8816 | 25.0278 | 3.7871 | 25.1648 | 5 | 26 | 46
Channu | 1977 | 5 | Monoblock | 4.0922 | 27.2727 | 5.7624 | 19.0002 | 5 | 26 | 46
Channu | 3415 | 5 | Monoblock | 4.0161 | 28.2663 | 5.8787 | 18.9436 | 5 | 26 | 46
Channu | 3389 | 5 | Monoblock | 5.0545 | 29.5955 | 5.1572 | 28.4549 | 5 | 26 | 46
Channu | New Connection | 5 | Monoblock | 4.3816 | 28.3822 | 5.8707 | 20.7807 | 5 | 26 | 46
Channu | 3365 | 5 | Monoblock | 5.2709 | 27.881 | 5.1763 | 27.8513 | 5 | 26 | 46
Channu | 3375 | 5 | Monoblock | 4.7555 | 23.298 | 5.3093 | 20.4712 | 5 | 26 | 46
Channu | 885 | 5 | Monoblock | 3.2962 | 15.4639 | 4.4875 | 11.1429 | 6 | 19 | 39
Channu | 3360 | 5 | Monoblock | 3.2738 | 14.7493 | 4.091 | 11.579 | 6 | 19 | 39
Channu | 3362 | 5 | Monoblock | 3.2524 | 22.779 | 4.7821 | 15.1978 | 5 | 26 | 46
Channu | 736 | 5 | Monoblock | 3.3977 | 29.654 | 6.1774 | 16.0005 | 5 | 26 | 46
Channu | 3367 | 5 | Monoblock | 3.6502 | 24.4366 | 4.85 | 18.0419 | 5 | 26 | 46
Channu | 3366 | 5 | Monoblock | 3.4066 | 30.0802 | 7.1188 | 14.1211 | 5 | 26 | 46
Channu | 3433 | 5 | Monoblock | 3.7958 | 27.4223 | 4.7773 | 21.3747 | 5 | 26 | 46
Channu | 1972 | 5 | Monoblock | 5.7534 | 26.6115 | 4.8537 | 30.9449 | 5 | 26 | 46
Channu | 7 | 7.5 | Monoblock | 4.2338 | 26.2544 | 6.9857 | 15.6098 | 5 | 26 | 46
Channu | 942 | 5 | Monoblock | 3.8646 | 32.3741 | 6.01 | 20.422 | 5 | 26 | 46
Channu | 3462 | 5 | Monoblock | 3.9765 | 28.8 | 5.2494 | 21.402 | 5 | 26 | 46
Channu | 17 | 7.5 | Monoblock | 5.1983 | 27.4893 | 6.0507 | 23.1677 | 5 | 26 | 46
Channu | 15 |  | Monoblock | 5.4091 | 23.6097 | 6.1582 | 20.3439 | 6 | 24.5 | 51
Channu | 14 | 7.5 | Monoblock | 6.6295 | 23.1481 | 9.3473 | 16.1057 | 7 | 22.5 | 56
Channu | 1 | 10 | Monoblock | 3.9787 | 26.393 | 6.7344 | 15.2969 | 5 | 26 | 46
Channu | 903 | 7.5 | Monoblock | 3.9302 | 26.3158 | 6.4244 | 15.7933 | 5 | 26 | 46
Channu | 3453 | 5 | Monoblock | 4.2753 | 25.6337 | 5.7113 | 18.8241 | 5 | 26 | 46
Channu | New Connection | 5 | Monoblock | 4.3574 | 19.9137 | 5.3492 | 15.913 | 5 | 26 | 46
Channu | 3394 | 5 | Monoblock | 5.6651 | 22.1839 | 5.6007 | 22.0125 | 6 | 19 | 39
Channu | 3371 | 5 | Monoblock | 5.9966 | 22.2938 | 4.7427 | 27.6525 | 6 | 19 | 39
Channu | 21 | 7.5 | Monoblock | 4.0963 | 32.1429 | 8.1114 | 15.924 | 5 | 26 | 46
Channu | 764 | 5 | Monoblock | 4.8887 | 28.6898 | 6.2831 | 21.8987 | 5 | 26 | 46
Channu | 3361 | 5 | Monoblock | 5.0609 | 27.8638 | 4.8767 | 28.3669 | 5 | 26 | 46
Channu | 1089 | 5 | Monoblock | 4.0803 | 25.0417 | 4.7091 | 21.2856 | 5 | 26 | 46
Channu | 941 | 7.5 | Monoblock | 5.333 | 33.4821 | 6.6604 | 26.2996 | 5 | 26 | 46
Channu | New Connection |  | Monoblock | 3.7966 | 12.3069 | 3.339 | 13.7276 | 5 | 26 | 46
Channu | 23 | 7.5 | Monoblock | 3.7349 | 30.8219 | 5.8903 | 19.1721 | 5 | 26 | 46
Channu | 3382 | 5 | Monoblock | 5.6887 | 18.9913 | 4.8483 | 21.8601 | 6 | 19 | 39
Channu | 3416 | 7.5 | Monoblock | 6.9918 | 16.06 | 5.8836 | 18.7222 | 7 | 18.5 | 43
Channu | 20 |  | Monoblock | 5.0569 | 28.5714 | 4.2953 | 32.9984 | 5 | 26 | 46
Channu | 3419 | 5 | Monoblock | 3.3752 | 18.4464 | 3.5485 | 17.2119 | 5 | 26 | 46
Channu | 3417 | 5 | Monoblock | 4.6528 | 26.7142 | 5.7719 | 21.1255 | 5 | 26 | 46
Channu | 943 | 5 | Monoblock | 3.4099 | 18.6838 | 5.4479 | 11.4722 | 5 | 26 | 46
Channu | 3430 |  | Monoblock | 4.9864 | 26.3466 | 6.3436 | 20.3165 | 5 | 26 | 46
Channu | 4 | 15 | Monoblock | 6.3072 | 20.9497 | 6.2033 | 20.8957 | 7 | 18.5 | 43
Channu | 1966 | 5 | Monoblock | 4.8918 | 18.1598 | 4.8935 | 17.8083 | 5 | 26 | 46
Channu | 961 | 5 | Monoblock | 5.3135 | 27.2975 | 5.3509 | 26.5916 | 5 | 26 | 46
Channu | 16 | 7.5 | Monoblock | 6.3376 | 24.4565 | 6.0821 | 24.9997 | 7 | 22.5 | 56
Channu | 3370 | 5 | Monoblock | 3.8829 | 23.5726 | 4.0742 | 22.0388 | 5 | 26 | 46
Channu | 24 | 5 | Monoblock | 5.7782 | 16.7535 | 3.6711 | 25.8686 | 7 | 22.5 | 56
Channu | 3456 | 5 | Monoblock | 6.7955 | 19.8238 | 7.1432 | 18.5007 | 7 | 22.5 | 56
Channu | 3439 | 5 | Monoblock | 4.0398 | 20.6517 | 3.0199 | 27.1012 | 5 | 26 | 46
Channu | 28 | 5 | Monoblock | 3.4256 | 19.4763 | 4.3056 | 15.2013 | 5 | 26 | 46
Channu | 2 | 5 | Monoblock | 5.7698 | 17.7235 | 3.6451 | 27.5214 | 7 | 22.5 | 56
Channu | 1005 | 5 | Monoblock | 4.5046 | 23.3402 | 5.5001 | 18.7525 | 5 | 26 | 46
Channu | 3436 | 5 | Monoblock | 5.7163 | 24.1935 | 6.0406 | 22.4597 | 7 | 22.5 | 56
Channu | 22 | 5 | Monoblock | 4.9473 | 25.6191 | 5.3573 | 23.209 | 5 | 26 | 46
Channu | 3449 | 5 | Monoblock | 4.4444 | 24.4233 | 4.678 | 22.7628 | 5 | 26 | 46
Channu | 29 | 5 | Monoblock | 3.8443 | 21.2766 | 5.2303 | 15.3413 | 5 | 26 | 46
Channu | 3408 | 5 | Monoblock | 2.6405 | 22.927 | 5.0959 | 11.6542 | 5 | 26 | 46
Channu | 1232 | 7.5 | Monoblock | 3.4608 | 20.6517 | 4.5238 | 15.4986 | 5 | 26 | 46
Channu | 1978 |  | Monoblock | 4.2332 | 31.6011 | 6.0668 | 21.6313 | 5 | 26 | 46
Channu | 3384 |  | Monoblock | 6.8688 | 20.7708 | 6.5246 | 21.4511 | 7 | 22.5 | 56
Channu | 3369 | 5 | Monoblock | 3.9752 | 18.711 | 4.7871 | 15.2422 | 5 | 26 | 46
Channu | 1964 | 5 | Monoblock | 2.5978 | 21.3751 | 6.2794 | 8.6749 | 5 | 26 | 46
Channu | 1970 | 5 | Monoblock | 4.2031 | 24.6305 | 4.0396 | 25.1404 | 5 | 26 | 46
Channu | 1968 | 5 | Monoblock | 4.2335 | 24.3969 | 7.2586 | 13.959 | 5 | 26 | 46
Channu | 1967 | 5 | Monoblock | 3.5471 | 23.2108 | 4.0577 | 19.9045 | 5 | 26 | 46
Channu | 3425 | 5 | Monoblock | 2.9027 | 22.7273 | 3.8111 | 16.9811 | 5 | 26 | 46
Channu | 3458 | 5 | Monoblock | 3.4114 | 26.6667 | 6.363 | 14.0251 | 5 | 26 | 46
Channu | 3364 | 5 | Monoblock | 3.489 | 17.9069 | 3.8254 | 16.0221 | 5 | 26 | 46
Channu | 3468 | 5 | Monoblock | 5.0676 | 22.7848 | 3.7789 | 29.9742 | 5 | 26 | 46
Channu | 784 | 5 | Monoblock | 4.4077 | 22.596 | 5.7896 | 16.8759 | 5 | 26 | 46
Channu | 1963 | 5 | Monoblock | 4.4761 | 23.012 | 4.9719 | 20.3235 | 5 | 26 | 46
Channu | 3358 | 5 | Monoblock | 3.306 | 22.2277 | 4.7341 | 15.2276 | 5 | 26 | 46
Channu | New Connection | 5 | Monoblock | 4.1312 | 28.7816 | 5.2038 | 22.4154 | 5 | 26 | 46
Channu | 6 | 5 | Monoblock | 2.7666 | 22.4719 | 5.222 | 11.6796 | 5 | 26 | 46
Channu | 1017 |  | Monoblock | 3.7136 | 20.5011 | 4.9863 | 14.9785 | 5 | 26 | 46
Channu | 3414 | 5 | Monoblock | 2.8009 | 19.7066 | 2.9657 | 18.2581 | 5 | 26 | 46
Channu | 3428 | 5 | Monoblock | 5.0104 | 11.7894 | 4.5526 | 12.7284 | 5 | 26 | 46
Channu | 3390 | 5 | Monoblock | 3.5694 | 24.855 | 4.852 | 17.9377 | 5 | 26 | 46
Channu | 18 | 5 | Monoblock | 3.6046 | 23.9872 | 5.2068 | 16.2906 | 5 | 26 | 46
Channu | 3442 | 5 | Monoblock | 4.1721 | 23.7404 | 3.339 | 29.1008 | 5 | 26 | 46
Channu | 53 | 5 | Monoblock | 3.154 | 33.7079 | 6.6084 | 15.7823 | 6 | 33 | 40
Channu | 3432 | 5 | Monoblock | 4.2031 | 28.0811 | 6.3397 | 18.2636 | 5 | 26 | 46
Channu | 3441 | 5 | Monoblock | 5.7418 | 31.2609 | 5.22 | 33.7329 | 6 | 33 | 40
Channu | 1962 | 5 | Monoblock | 4.4736 | 22.0103 | 4.4175 | 21.8661 | 5 | 26 | 46
Channu | 3443 | 5 | Monoblock | 3.7381 | 20.2384 | 4.4521 | 16.6701 | 5 | 26 | 46
Channu | 3465 | 5 | Monoblock | 6.3451 | 25.395 | 5.3677 | 29.4484 | 7 | 22.5 | 56
Channu | 3373 | 5 | Monoblock | 4.4077 | 22.596 | 5.7896 | 16.8759 | 5 | 26 | 46
Channu | 3405 |  | Monoblock | 5.0601 | 30.2115 | 4.0023 | 37.4703 | 5 | 26 | 46
Channu | 3447 | 5 | Monoblock | 8.8939 | 19.2308 | 4.3946 | 38.1804 | 9 | 17 | 50
Channu | 3444 | 5 | Monoblock | 2.1979 | 20.2657 | 4.5534 | 9.5964 | 5 | 26 | 46
Channu | 3380 | 5 | Monoblock | 3.2435 | 23.071 | 4.9358 | 14.8728 | 5 | 26 | 46
Channu | 1181 |  | Monoblock | 3.7617 | 20.6992 | 6.0668 | 12.5907 | 5 | 26 | 46
Channu | 3402 |  | Monoblock | 4.552 | 17.5131 | 3.3961 | 23.0276 | 5 | 26 | 46
Channu | 3454 |  | Monoblock | 5.4418 | 23.1899 | 6.6991 | 18.4794 | 5 | 26 | 46
Channu | 1974 | 5 | Monoblock | 3.148 | 17.1233 | 4.8185 | 10.9743 | 5 | 26 | 46
Channu | 543 |  | Monoblock | 3.4196 | 20.3252 | 3.8139 | 17.8777 | 5 | 26 | 46
Channu | 3413 | 5 | Monoblock | 4.0068 | 19.698 | 4.531 | 17.088 | 5 | 26 | 46
Channu | 3440 | 5 | Monoblock | 2.6282 | 29.1734 | 4.5219 | 16.6338 | 5 | 26 | 46
Channu | 3463 | 5 | Monoblock | 7.5217 | 13.6199 | 4.5211 | 22.2287 | 8 | 13.5 | 36
Channu | 882 |  | Monoblock | 5.7173 | 22.579 | 4.4421 | 28.5089 | 7 | 22.5 | 56
Channu | 571 | 5 | Monoblock | 5.5706 | 19.2308 | 4.3946 | 23.9139 | 7 | 22.5 | 56
Channu | 1938 |  | Monoblock | 4.1483 | 21.9031 | 5.1167 | 17.4201 | 5 | 26 | 46
Channu | 2130 |  | Monoblock | 6.4338 | 24.1093 | 6.6007 | 23.0534 | 7 | 22.5 | 56
Channu | 2868 | 7.5 | Monoblock | 6.4965 | 27.5229 | 7.5471 | 23.2415 | 7 | 22.5 | 56
Channu | 2863 | 5 | Monoblock | 4.8605 | 20.7565 | 4.9212 | 20.1112 | 5 | 26 | 46
Channu | 830 |  | Monoblock | 7.058 | 26.1097 | 4.1895 | 43.1506 | 7 | 22.5 | 56
Channu | 2888 |  | Monoblock | 6.1578 | 24.0128 | 6.6813 | 21.7108 | 7 | 22.5 | 56
Channu | 2861 |  | Monoblock | 6.9549 | 20.5479 | 4.1735 | 33.5917 | 7 | 22.5 | 56
Channu | 994 |  | Monoblock | 7.8908 | 22.1293 | 5.2221 | 32.8029 | 8 | 20 | 59
Channu | 546 |  | Monoblock | 4.7419 | 27.9764 | 6.3532 | 20.484 | 5 | 26 | 46
Channu | 770 | 7.5 | Monoblock | 5.8036 | 38.0228 | 7.7603 | 27.8951 | 5 | 26 | 46
Channu | 34 | 5 | Monoblock | 5.0847 | 27.7264 | 7.0066 | 19.7386 | 5 | 26 | 46
Channu | 544 | 7.5 | Monoblock | 5.6333 | 20.595 | 6.3368 | 17.9608 | 7 | 22.5 | 56
Channu | 769 | 7.5 | Monoblock | 6.9917 | 36.9004 | 6.8036 | 37.2001 | 7 | 22.5 | 56
Channu | 997 | 5 | Monoblock | 5.7996 | 27.5651 | 7.134 | 21.9832 | 7 | 22.5 | 56
Channu | 2886 | 7.5 | Monoblock | 7.1325 | 25.413 | 7.0268 | 25.3051 | 7 | 22.5 | 56
Channu | 1928 | 5 | Monoblock | 6.8533 | 27.027 | 6.0774 | 29.8984 | 7 | 22.5 | 56
Channu | 1937 | 5 | Monoblock | 5.541 | 24.9861 | 5.1173 | 26.5412 | 7 | 22.5 | 56
Channu | 1927 | 5 | Monoblock | 7.0578 | 18.1671 | 4.3416 | 28.9715 | 7 | 22.5 | 56
Channu | 2877 | 7.5 | Monoblock | 7.8812 | 23.3524 | 6.1484 | 29.3652 | 8 | 20 | 59
Channu | 2136 | 5 | Monoblock | 4.9991 | 28.3197 | 5.8645 | 23.6822 | 5 | 26 | 46
Channu | 2862 | 5 | Monoblock | 4.0899 | 27.8035 | 6.1545 | 18.1254 | 5 | 26 | 46
Channu | 2867 | 5 | Monoblock | 4.0766 | 27.3556 | 4.9092 | 22.2846 | 5 | 26 | 46
Channu | 2135 | 5 | Monoblock | 4.0172 | 23.0003 | 3.8753 | 23.3895 | 5 | 26 | 46
Channu | 2864 | 5 | Monoblock | 3.6014 | 16.4264 | 4.7104 | 12.3203 | 5 | 26 | 46
Channu | 1919 | 5 | Monoblock | 7.0724 | 22.0049 | 5.0464 | 30.2531 | 7 | 22.5 | 56
Channu | 2138 | 5 | Submersible | 6.4895 | 22.0426 | 6.0411 | 23.2288 | 8 | 73 | 63
Channu | 2143 | 5 | Submersible | 6.0431 | 23.7718 | 4.9629 | 28.3959 | 6 | 77 | 61
Channu | 2134 | 5 | Monoblock | 5.2619 | 22.7848 | 3.7789 | 31.1234 | 5 | 26 | 46
Channu | 2133 | 5 | Submersible | 5.5695 | 23.7906 | 6.3476 | 20.4779 | 8 | 73 | 63
Channu | 1929 | 5 | Monoblock | 6.2185 | 23.1125 | 3.3149 | 42.5335 | 7 | 22.5 | 56
Channu | New Connection | 5 | Monoblock | 4.4157 | 32.0399 | 5.0149 | 27.6752 | 5 | 26 | 46
Channu | 43 | 5 | Monoblock | 4.0134 | 22.4439 | 4.2507 | 20.7884 | 5 | 26 | 46
Channu | 859 | 5 | Monoblock | 5.2064 | 21.7024 | 4.1279 | 26.8525 | 5 | 26 | 46
Channu | 44 | 5 | Monoblock | 6.6419 | 15.015 | 3.9563 | 24.7282 | 7 | 22.5 | 56
Channu | 46 | 5 | Monoblock | 5.8727 | 22.5677 | 4.5246 | 28.735 | 7 | 22.5 | 56
Channu | 2878 | 5 | Monoblock | 6.0152 | 25.9815 | 3.66 | 41.8898 | 7 | 22.5 | 56
Channu | 781 | 5 | Monoblock | 3.9344 | 21.4388 | 4.12 | 20.0839 | 5 | 26 | 46
Channu | 2825 | 5 | Monoblock | 4.7233 | 21.7024 | 4.1255 | 24.3751 | 5 | 26 | 46
Channu | 1922 | 5 | Monoblock | 5.0622 | 13.8058 | 2.9554 | 23.1979 | 5 | 26 | 46
Channu | 705 | 5 | Monoblock | 4.4117 | 24.4233 | 4.5005 | 23.4865 | 5 | 26 | 46
Channu | 2879 | 5 | Monoblock | 4.2377 | 23.9808 | 4.9869 | 19.9912 | 5 | 26 | 46
Channu | New Connection | 5 | Monoblock | 5.3988 | 23.3221 | 4.1574 | 29.7106 | 7 | 22.5 | 56
Channu | 33 |  | Monoblock | 5.8715 | 25.3022 | 3.0855 | 47.234 | 7 | 22.5 | 56
Channu | 2893 |  | Monoblock | 7.9625 | 17.9069 | 3.8972 | 35.8904 | 8 | 17.8 | 47
Channu | 39 | 7.5 | Monoblock | 7.419 | 25.7216 | 6.1436 | 30.4712 | 7 | 22.5 | 56
Channu | 2871 | 5 | Monoblock | 7.7911 | 21.1268 | 6.1673 | 26.1822 | 8 | 17.8 | 47
Channu | 40 | 5 | Monoblock | 6.4524 | 25.2525 | 6.3471 | 25.1836 | 7 | 22.5 | 56
Channu | 48 | 5 | Monoblock | 5.9205 | 26.3543 | 4.3766 | 34.9737 | 7 | 22.5 | 56
Channu | 1936 | 5 | Monoblock | 5.8294 | 17.3846 | 5.1523 | 19.2956 | 7 | 22.5 | 56
Channu | 1934 | 5 | Monoblock | 3.5959 | 23.7969 | 5.0811 | 16.5209 | 5 | 26 | 46
Channu | 2869 | 5 | Submersible | 6.5634 | 16.1551 | 5.7127 | 18.2083 | 6 | 60 | 80
Channu | 41 | 5 | Monoblock | 9.7675 | 29.7226 | 6.6517 | 42.8158 | 10 | 28 | 59
Channu | 2132 | 5 | Monoblock | 6.5563 | 21.7918 | 4.8854 | 28.6893 | 7 | 22.5 | 56
Channu | 2887 |  | Monoblock | 5.2579 | 41.0771 | 6.2427 | 33.9396 | 5 | 26 | 46
Channu | 1930 | 5 | Monoblock | 4.7861 | 19.1123 | 4.4487 | 20.1714 | 5 | 26 | 46
Channu | 794 | 5 | Monoblock | 6.3804 | 23.012 | 4.4864 | 32.1055 | 6 | 24.5 | 51
Channu | 2892 | 5 | Monoblock | 5.3376 | 27.933 | 4.8415 | 30.2103 | 5 | 26 | 46
Channu | 2891 | 5 | Monoblock | 5.4514 | 16.2162 | 3.348 | 25.9024 | 7 | 22.5 | 56
Channu | 1131 | 5 | Monoblock | 2.8033 | 19.1489 | 4.2617 | 12.3568 | 5 | 26 | 46
Channu | 2137 | 5 | Monoblock | 5.0909 | 15.2827 | 3.8076 | 20.045 | 5 | 26 | 46
Channu | 0 | 5 | Monoblock | 5.4367 | 17.0197 | 4.239 | 21.4138 | 5 | 26 | 46
Channu | New Connection | 5 | Monoblock | 4.1877 | 28.0987 | 4.4774 | 25.7816 | 5 | 26 | 46
Channu | 2875 | 5 | Monoblock | 4.7087 | 24.7729 | 3.9242 | 29.1609 | 5 | 26 | 46
Channu | 47 | 5 | Monoblock | 5.1439 | 16.2455 | 4.7924 | 17.1055 | 5 | 26 | 46
Channu | 2131 | 5 | Monoblock | 5.5893 | 22.579 | 4.4418 | 27.8726 | 6 | 24.5 | 51
Channu | 674 | 5 | Monoblock | 6.1453 | 18.105 | 4.3692 | 24.9809 | 6 | 24.5 | 51
Channu | 2142 | 5 | Monoblock | 4.4913 | 14.6819 | 3.3629 | 19.2357 | 5 | 26 | 46
Channu | 2880 | 5 | Monoblock | 3.4962 | 22.6757 | 4.9161 | 15.82 | 5 | 26 | 46
Channu | 2866 | 5 | Monoblock | 3.1219 | 30.8642 | 7.1134 | 13.2882 | 5 | 26 | 46
Channu | 1921 | 5 | Monoblock | 4.9729 | 23.7404 | 5.843 | 19.8213 | 5 | 26 | 46
Channu | New Connection | 7.5 | Monoblock | 4.7929 | 36.9914 | 7.8725 | 22.0928 | 5 | 26 | 46
Channu | 1920 | 5 | Monoblock | 4.9864 | 27.8638 | 5.5276 | 24.6585 | 5 | 26 | 46
Channu | 35 | 5 | Monoblock | 7.3925 | 19.8413 | 5.3284 | 27.0042 | 7 | 18.5 | 43
Channu | 1164 |  | Monoblock | 2.3564 | 24.2326 | 4.714 | 11.8827 | 5 | 26 | 46
Channu | 1134 | 5 | Monoblock | 4.2091 | 23.8727 | 3.3301 | 29.6009 | 5 | 26 | 46
Channu | 425 | 10 | Monoblock | 4.5347 | 23.9808 | 3.2414 | 32.9121 | 5 | 26 | 46
Channu | 1150 |  | Monoblock | 4.5848 | 26.7221 | 3.2793 | 36.6506 | 5 | 26 | 46
Channu | 654 |  | Monoblock | 4.6849 | 10.989 | 3.6982 | 13.6564 | 5 | 26 | 46
Channu | 3351 | 5 | Monoblock | 3.5532 | 38.8601 | 3.9227 | 34.5301 | 5 | 26 | 46
Channu | 3292 | 5 | Monoblock | 3.7792 | 21.6086 | 2.9221 | 27.416 | 5 | 26 | 46
Channu | 1149 | 5 | Monoblock | 2.5852 | 20.7804 | 3.7232 | 14.1545 | 5 | 26 | 46
Channu | 410 | 5 | Monoblock | 4.2239 | 39.0964 | 5.1645 | 31.3683 | 5 | 26 | 46
Channu | 3303 | 5 | Monoblock | 5.0558 | 21.6606 | 3.9517 | 27.1859 | 5 | 26 | 46
Channu | 1066 | 5 | Monoblock | 5.3035 | 28.0987 | 9.1333 | 16.0061 | 5 | 26 | 46
Channu | 707 | 5 | Monoblock | 5.2717 | 19.3798 | 3.1088 | 32.2394 | 5 | 26 | 46
Channu | 1148 | 5 | Monoblock | 4.0557 | 27.3473 | 4.815 | 22.5971 | 5 | 26 | 46
Channu | 612 | 7.5 | Monoblock | 4.4699 | 32.1314 | 3.7374 | 37.6991 | 5 | 26 | 46
Channu | 408 | 5 | Monoblock | 5.8641 | 19.9689 | 5.2206 | 22.0042 | 6 | 24.5 | 51
Channu | 405 | 7.5 | Monoblock | 4.9092 | 41.8799 | 5.304 | 38.0264 | 5 | 26 | 46
Channu | 564 | 7.5 | Monoblock | 3.621 | 37.9747 | 4.4149 | 30.5545 | 5 | 26 | 46
Channu | 1127 | 5 | Monoblock | 3.6482 | 24.0706 | 5.8551 | 14.713 | 5 | 26 | 46
Channu | 911 | 5 | Monoblock | 3.6186 | 27.7949 | 4.7297 | 20.8614 | 5 | 26 | 46
Channu | 3288 | 5 | Monoblock | 4.0408 | 27.2562 | 3.5272 | 30.6318 | 5 | 26 | 46
Channu | 422 | 5 | Monoblock | 3.1582 | 26.9058 | 4.3003 | 19.3845 | 5 | 26 | 46
Channu | 1062 | 5 | Monoblock | 4.6169 | 30.3337 | 5.7168 | 24.0323 | 5 | 26 | 46
Channu | 3274 | 5 | Monoblock | 3.5401 | 22.5507 | 4.6849 | 16.7164 | 5 | 26 | 46
Channu | 865 | 5 | Monoblock | 4.5857 | 26.3312 | 4.7465 | 24.9562 | 5 | 26 | 46
Channu | 3295 | 5 | Monoblock | 3.4897 | 28.6078 | 4.7285 | 20.7118 | 5 | 26 | 46
Channu | 993 | 5 | Monoblock | 5.4049 | 23.1899 | 2.8226 | 43.5624 | 5 | 26 | 46
Channu | 2144 | 5 | Monoblock | 5.7638 | 24.1805 | 2.8677 | 47.6764 | 6 | 24.5 | 51
Channu | 1078 | 5 | Monoblock | 5.1658 | 17.9033 | 7.7023 | 11.7791 | 5 | 26 | 46
Channu | 1154 | 5 | Monoblock | 5.8054 | 24.5298 | 3.2996 | 42.3384 | 6 | 24.5 | 51
Channu | 3339 | 5 | Monoblock | 4.7779 | 22.4944 | 7.3479 | 14.3489 | 5 | 26 | 46
Channu | 1160 | 5 | Monoblock | 2.9185 | 22.2772 | 5.5163 | 11.5622 | 5 | 26 | 46
Channu | 1133 | 5 | Monoblock | 2.7675 | 29.8013 | 4.168 | 19.4121 | 5 | 26 | 46
Channu | sr. 361 | 5 | Monoblock | 3.6143 | 17.4452 | 3.564 | 17.3556 | 5 | 26 | 46
Channu | 793 | 7.5 | Monoblock | 4.4053 | 19.3632 | 4.918 | 17.015 | 5 | 26 | 46
Channu | 737 | 5 | Monoblock | 4.9815 | 33.8473 | 3.8885 | 42.5376 | 5 | 26 | 46
Channu | 3346 | 5 | Monoblock | 4.475 | 28.472 | 3.578 | 34.9334 | 5 | 26 | 46
Channu | 1165 | 5 | Monoblock | 3.1578 | 20.8478 | 2.8334 | 22.7936 | 5 | 26 | 46
Channu | 3299 | 5 | Monoblock | 2.8986 | 21.9673 | 4.0291 | 15.5034 | 5 | 26 | 46
Channu | 3343 | 5 | Submersible | 5.5186 | 15.8954 | 1.9055 | 45.1604 | 4 | 58 | 80
Channu | 1068 | 5 | Monoblock | 4.3296 | 25.6849 | 3.4052 | 32.0367 | 5 | 26 | 46
Channu | 404 | 10 | Monoblock | 4.235 | 24.6036 | 3.4021 | 30.0458 | 5 | 26 | 46
Channu | 3276 | 5 | Monoblock | 7.4209 | 28.6351 | 5.4062 | 38.5591 | 7 | 22.5 | 56
Channu | 432 | 5 | Monoblock | 4.0434 | 20.3989 | 4.0923 | 19.7723 | 5 | 26 | 46
Channu | 3302 | 5 | Monoblock | 4.2 | 32.1543 | 4.0505 | 32.7083 | 5 | 26 | 46
Channu | 1132 | 5 | Monoblock | 2.7213 | 26.6115 | 3.339 | 21.2766 | 5 | 26 | 46
Channu | 1075 | 5 | Monoblock | 3.0756 | 17.9069 | 3.7999 | 14.2185 | 5 | 26 | 46

## Shenakheda
Feeder Name | Account No. | Connected HP / Sanctioned Demand | Type of Pump | Existing Pump Set Measured Parameters |  |  |  | Energy Efficient Pump Sets Parameters
|  |  |  | Total Head (m) | Flow (l/s) | Power (kW) | Efficiency (%) | Head (m) | Flow (l/s) | Efficiency (%)
Shenakheda | 1069 | 5 | Monoblock | 2.8929 | 22.8368 | 2.9245 | 22.1604 | 2.8929 | 22.8368 | 56
Shenakheda | 451 | 5 | Monoblock | 2.7373 | 28.5714 | 4.206 | 18.2415 | 2.7373 | 28.5714 | 45
Shenakheda | New Connection | 5 | Monoblock | 5.2623 | 27.7094 | 4.5837 | 31.2073 | 5.2623 | 27.7094 | 45
Shenakheda | 402 | 5 | Monoblock | 3.7716 | 20.9497 | 4.067 | 19.059 | 3.7716 | 20.9497 | 58
Shenakheda | 456 | 5 | Monoblock | 3.1229 | 21.2064 | 4.3276 | 15.0124 | 3.1229 | 21.2064 | 58
Shenakheda | 3384 | 5 | Monoblock | 3.8124 | 20.6517 | 3.0038 | 25.7132 | 3.8124 | 20.6517 | 58
Shenakheda | New Connection | 5 | Monoblock | 4.2368 | 17.192 | 3.8157 | 18.7264 | 4.2368 | 17.192 | 60
Shenakheda | 3287 | 5 | Monoblock | 2.6 | 29.2873 | 3.6184 | 20.6447 | 2.6 | 29.2873 | 45
Shenakheda | 1053 | 5 | Monoblock | 3.1709 | 22.1511 | 3.1143 | 22.1252 | 3.1709 | 22.1511 | 56
Shenakheda | 1082 | 5 | Monoblock | 2.7392 | 26.1628 | 2.9788 | 23.6012 | 2.7392 | 26.1628 | 45
Shenakheda | 1020 | 5 | Monoblock | 3.0816 | 26.9623 | 3.4336 | 23.7385 | 3.0816 | 26.9623 | 45
Shenakheda | 3329 | 5 | Monoblock | 3.2822 | 23.1184 | 4.2235 | 17.6245 | 3.2822 | 23.1184 | 53
Shenakheda | 423 | 5 | Monoblock | 5.4452 | 17.2249 | 4.4233 | 20.8012 | 5.4452 | 17.2249 | 60
Shenakheda | 973 | 5 | Monoblock | 3.6446 | 25.4741 | 5.0488 | 18.0395 | 3.6446 | 25.4741 | 45
Shenakheda | 398 | 5 | Monoblock | 4.4129 | 22.2938 | 4.7408 | 20.3575 | 4.4129 | 22.2938 | 60
Shenakheda | 2157 | 5 | Monoblock | 3.3997 | 19.4763 | 3.4333 | 18.9188 | 3.3997 | 19.4763 | 60
Shenakheda | 3337 | 5 | Monoblock | 3.8991 | 16.1261 | 2.8274 | 21.8156 | 3.8991 | 16.1261 | 59
Shenakheda | 444 | 5 | Monoblock | 2.9378 | 22.6244 | 3.8236 | 17.0532 | 2.9378 | 22.6244 | 55
Shenakheda | 1067 | 5 | Monoblock | 3.3136 | 17.1756 | 2.6896 | 20.7582 | 3.3136 | 17.1756 | 60
Shenakheda | 3294 | 5 | Monoblock | 5.1456 | 24.5165 | 4.8396 | 25.5712 | 5.1456 | 24.5165 | 50
Shenakheda | 1056 | 5 | Monoblock | 2.8414 | 21.3371 | 3.475 | 17.1155 | 2.8414 | 21.3371 | 58
Shenakheda | 1057 | 5 | Monoblock | 5.4552 | 16.9078 | 3.398 | 26.6282 | 5.4552 | 16.9078 | 60
Shenakheda | 454 |  | Monoblock | 3.9927 | 28.8554 | 5.4367 | 20.7887 | 3.9927 | 28.8554 | 45
Shenakheda | 1085 | 5 | Monoblock | 4.6506 | 27.2562 | 3.4867 | 35.6641 | 4.6506 | 27.2562 | 45
Shenakheda | 1153 | 5 | Monoblock | 3.7364 | 27.2645 | 4.7567 | 21.0094 | 3.7364 | 27.2645 | 45
Shenakheda | 3285 | 5 | Monoblock | 3.2482 | 14.6819 | 3.3733 | 13.8685 | 3.2482 | 14.6819 | 58
Shenakheda | 407 | 5 | Monoblock | 5.1631 | 32.0285 | 3.3385 | 48.5909 | 5.1631 | 32.0285 | 50
Shenakheda | 1177 | 5 | Monoblock | 4.003 | 19.0194 | 4.8467 | 15.4104 | 4.003 | 19.0194 | 60
Shenakheda | 455 | 5 | Monoblock | 4.7474 | 22.113 | 5.1167 | 20.1272 | 4.7474 | 22.113 | 60
Shenakheda | 414 | 5 | Monoblock | 5.4908 | 24.3375 | 7.23 | 18.1319 | 5.4908 | 24.3375 | 53
Shenakheda | 3316 | 5 | Monoblock | 4.7879 | 27.8638 | 4.88 | 26.8184 | 4.7879 | 27.8638 | 45
Shenakheda | 3328 | 5 | Monoblock | 4.4238 | 27.3473 | 4.0567 | 29.2558 | 4.4238 | 27.3473 | 45
Shenakheda | 1142 | 5 | Monoblock | 3.8256 | 22.1022 | 4.1133 | 20.1655 | 3.8256 | 22.1022 | 60
Shenakheda | 426 | 5 | Monoblock | 3.6626 | 29.2588 | 5.0633 | 20.7626 | 3.6626 | 29.2588 | 45
Shenakheda | 427 | 5 | Monoblock | 3.7225 | 27.1903 | 7.05 | 14.0841 | 3.7225 | 27.1903 | 45
Shenakheda | 3282 | 5 | Monoblock | 3.954 | 22.9066 | 5.1067 | 17.3991 | 3.954 | 22.9066 | 60
Shenakheda | 1176 | 5 | Monoblock | 2.6701 | 16.0456 | 3.2867 | 12.788 | 2.6701 | 16.0456 | 59
Shenakheda | 1128 | 5 | Monoblock | 3.8417 | 14.3954 | 3.44 | 15.771 | 3.8417 | 14.3954 | 58
Shenakheda | 2152 | 5 | Monoblock | 3.1895 | 22.113 | 6.0867 | 11.3674 | 3.1895 | 22.113 | 60
Shenakheda | 403 | 5 | Monoblock | 5.5307 | 19.5355 | 6.1933 | 17.1139 | 5.5307 | 19.5355 | 60
Shenakheda | New Connection | 5 | Monoblock | 4.5098 | 24.3046 | 5.8933 | 18.2455 | 4.5098 | 24.3046 | 53
Shenakheda | 452 | 5 | Monoblock | 3.015 | 24.4167 | 5.27 | 13.7034 | 3.015 | 24.4167 | 53
Shenakheda | 421 | 5 | Monoblock | 4.0357 | 19.7585 | 4.8467 | 16.1398 | 4.0357 | 19.7585 | 60
Shenakheda | 442 |  | Monoblock | 3.5186 | 13.4529 | 3.1615 | 14.688 | 3.5186 | 13.4529 | 58
Shenakheda | 849 | 5 | Monoblock | 4.0505 | 27.8638 | 5.535 | 20.0034 | 4.0505 | 27.8638 | 45
Shenakheda | 413 | 5 | Monoblock | 4.3499 | 20.7517 | 3.4931 | 25.3512 | 4.3499 | 20.7517 | 58
Shenakheda | 411 | 5 | Monoblock | 4.2665 | 28.8 | 5.2533 | 22.9455 | 4.2665 | 28.8 | 45
Shenakheda | 1081 | 5 | Monoblock | 4.757 | 22.5677 | 4.17 | 25.2553 | 4.757 | 22.5677 | 60
Shenakheda | 440 | 5 | Monoblock | 5.5968 | 20.6992 | 6.06 | 18.7539 | 5.5968 | 20.6992 | 58
Shenakheda | 448 |  | Monoblock | 3.9954 | 26.738 | 5.3622 | 19.5439 | 3.9954 | 26.738 | 45
Shenakheda | 2158 | 5 | Monoblock | 4.7735 | 14.1044 | 4.0391 | 16.3521 | 4.7735 | 14.1044 | 58
Shenakheda | 895 |  | Monoblock | 3.3908 | 22.7848 | 3.7789 | 20.0559 | 3.3908 | 22.7848 | 60
Shenakheda | 412 | 5 | Monoblock | 3.4852 | 21.5621 | 4.9099 | 15.0147 | 3.4852 | 21.5621 | 58
Shenakheda | 1166 | 5 | Monoblock | 5.4076 | 32.2234 | 3.7827 | 45.1897 | 5.4076 | 32.2234 | 50
Shenakheda | 430 | 5 | Monoblock | 5.697 | 23.3584 | 4.32 | 30.2185 | 5.697 | 23.3584 | 60
Shenakheda | New Connection | 5 | Monoblock | 5.3193 | 22.3436 | 3.8783 | 30.0635 | 5.3193 | 22.3436 | 58
Shenakheda | 701 | 5 | Monoblock | 3.0164 | 17.1625 | 3.5 | 14.51 | 3.0164 | 17.1625 | 60
Shenakheda | 3270 | 5 | Monoblock | 4.0955 | 12.3203 | 4.0167 | 12.3235 | 4.0955 | 12.3203 | 55
Shenakheda | 1060 | 5 | Monoblock | 2.5802 | 22.8195 | 4.6567 | 12.4035 | 2.5802 | 22.8195 | 60
Shenakheda | New Connection | 5 | Monoblock | 5.355 | 21.6972 | 4.48 | 25.4419 | 5.355 | 21.6972 | 58
Shenakheda | 400 | 5 | Submersible | 3.1782 | 29.615 | 6.8426 | 13.4941 | 3.1782 | 29.615 | 45
Shenakheda | 1130 | 5 | Monoblock | 3.9319 | 17.7235 | 3.6451 | 18.7549 | 3.9319 | 17.7235 | 60
Shenakheda | 446 | 5 | Monoblock | 3.1664 | 17.7235 | 3.6467 | 15.0968 | 3.1664 | 17.7235 | 60
Shenakheda | 443 | 5 | Monoblock | 2.5632 | 21.6972 | 4.8767 | 11.1873 | 2.5632 | 21.6972 | 58
Shenakheda | 1086 | 5 | Monoblock | 5.3313 | 23.1899 | 2.8554 | 42.475 | 5.3313 | 23.1899 | 60
Shenakheda | 3263 | 5 | Monoblock | 5.2677 | 19.9424 | 3.9753 | 25.9239 | 5.2677 | 19.9424 | 60
Shenakheda | 1124 | 5 | Monoblock | 5.8229 | 31.9602 | 3.2003 | 57.0457 | 5.8229 | 31.9602 | 50
Shenakheda | New Connection | 5 | Monoblock | 6.8212 | 16.7535 | 3.593 | 31.2017 | 6.8212 | 16.7535 | 60
Shenakheda | 3347 | 5 | Monoblock | 6.5891 | 21.449 | 3.8546 | 35.9687 | 6.5891 | 21.449 | 58
Shenakheda | 1104 | 5 | Monoblock | 3.7909 | 19.5143 | 3.1172 | 23.2805 | 3.7909 | 19.5143 | 60
Shenakheda | New Connection | 5 | Monoblock | 5.4731 | 18.7071 | 4.902 | 20.4898 | 5.4731 | 18.7071 | 60
Shenakheda | 1139 |  | Monoblock | 3.4109 | 12.6707 | 3.2326 | 13.1154 | 3.4109 | 12.6707 | 57
Shenakheda | 2148 | 5 | Monoblock | 3.0381 | 24.9032 | 3.6548 | 20.3081 | 3.0381 | 24.9032 | 50
Shenakheda | 876 | 5 | Monoblock | 2.5147 | 20.436 | 4.2475 | 11.8692 | 2.5147 | 20.436 | 60
Shenakheda | 1071 | 5 | Monoblock | 4.3656 | 20.6992 | 3.6521 | 24.2729 | 4.3656 | 20.6992 | 58
Shenakheda | New Connection |  | Monoblock | 4.3978 | 21.3574 | 3.7785 | 24.3857 | 4.3978 | 21.3574 | 58
Shenakheda | 1079 | 5 | Monoblock | 2.4979 | 20.7756 | 4.1859 | 12.1621 | 2.4979 | 20.7756 | 58
Shenakheda | 1061 | 5 | Monoblock | 6.0867 | 17.4452 | 3.5644 | 29.2238 | 6.0867 | 17.4452 | 60
Shenakheda | 2156 | 5 | Monoblock | 7.0355 | 19.8939 | 4.5899 | 29.9139 | 7.0355 | 19.8939 | 60
Shenakheda | New Connection | 5 | Monoblock | 5.8668 | 21.2064 | 4.3276 | 28.2028 | 5.8668 | 21.2064 | 58
Shenakheda | 2146 | 5 | Monoblock | 5.3311 | 20.2657 | 4.553 | 23.278 | 5.3311 | 20.2657 | 60
Shenakheda | 1065 | 5 | Monoblock | 4.9474 | 20.2657 | 4.5534 | 21.6012 | 4.9474 | 20.2657 | 60
Shenakheda | 3312 |  | Monoblock | 4.8488 | 17.1363 | 3.2126 | 25.3728 | 4.8488 | 17.1363 | 60
Shenakheda | 1135 | 5 | Monoblock | 3.9237 | 17.1233 | 4.8185 | 13.6785 | 3.9237 | 17.1233 | 60
Shenakheda | 1011 | 5 | Monoblock | 4.9271 | 21.5724 | 5.0116 | 20.8061 | 4.9271 | 21.5724 | 58
Shenakheda | 3278 | 5 | Monoblock | 2.7797 | 19.4805 | 2.9125 | 18.2385 | 2.7797 | 19.4805 | 60
Shenakheda | 1103 | 5 | Monoblock | 2.7275 | 18.6528 | 2.8839 | 17.3062 | 2.7275 | 18.6528 | 60
Shenakheda | 424 | 5 | Monoblock | 2.7223 | 18.1123 | 4.3841 | 11.0329 | 2.7223 | 18.1123 | 60
Shenakheda | New Connection | 5 | Monoblock | 5.605 | 27.4307 | 5.7887 | 26.0555 | 5.605 | 27.4307 | 45
Shenakheda | 104 | 7.5 | Monoblock | 4.9397 | 32.0171 | 3.8433 | 40.3684 | 4.9397 | 32.0171 | 50
Shenakheda | 94 | 5 | Monoblock | 5.3283 | 35.1014 | 5.7002 | 32.1878 | 5.3283 | 35.1014 | 45
Shenakheda | 119 | 7.5 | Monoblock | 4.297 | 25.7069 | 6.3566 | 17.0473 | 4.297 | 25.7069 | 45
Shenakheda | 652 | 5 | Monoblock | 4.2809 | 25.3807 | 3.1612 | 33.7174 | 4.2809 | 25.3807 | 50
Shenakheda | 113 |  | Monoblock | 5.7676 | 17.0197 | 3.654 | 26.3544 | 5.7676 | 17.0197 | 60
Shenakheda | 126 | 5 | Monoblock | 5.3008 | 21.7024 | 4.5228 | 24.9523 | 5.3008 | 21.7024 | 58
Shenakheda | 128 | 5 | Monoblock | 4.6878 | 26.3852 | 5.9611 | 20.355 | 4.6878 | 26.3852 | 50
Shenakheda | New Connection | 5 | Monoblock | 3.7365 | 20.6517 | 2.9129 | 25.9873 | 3.7365 | 20.6517 | 58
Shenakheda | 675 | 5 | Monoblock | 4.8765 | 28.1294 | 3.3394 | 40.2972 | 4.8765 | 28.1294 | 50
Shenakheda | 118 | 10 | Monoblock | 4.1098 | 20.1387 | 4.5219 | 17.9557 | 4.1098 | 20.1387 | 58
Shenakheda | 1047 | 5 | Monoblock | 4.4355 | 32.2234 | 5.2443 | 26.7362 | 4.4355 | 32.2234 | 55
Shenakheda | 2218 | 5 | Monoblock | 4.5462 | 30.3132 | 3.6393 | 37.1478 | 4.5462 | 30.3132 | 50
Shenakheda | 659 | 5/7.5 | Monoblock | 4.8983 | 30.4672 | 3.1011 | 47.2093 | 4.8983 | 30.4672 | 50
Shenakheda | 2224 | 5 | Monoblock | 4.209 | 27.2645 | 4.6233 | 24.3492 | 4.209 | 27.2645 | 50
Shenakheda | 2519 | 5 | Monoblock | 4.3453 | 26.2927 | 5.5123 | 20.3326 | 4.3453 | 26.2927 | 50
Shenakheda | New Connection | 5 | Monoblock | 3.911 | 24.0192 | 3.6421 | 25.3023 | 3.911 | 24.0192 | 52
Shenakheda | 1940 | 5 | Monoblock | 3.9898 | 30.8748 | 5.1967 | 23.2537 | 3.9898 | 30.8748 | 56
Shenakheda | New Connection | 5 | Monoblock | 3.9839 | 23.9044 | 7.34 | 12.7281 | 3.9839 | 23.9044 | 52
Shenakheda | 120 | 10 | Monoblock | 4.3418 | 32.1773 | 5.6379 | 24.3089 | 4.3418 | 32.1773 | 55
Shenakheda | 725 | 5 | Monoblock | 3.5797 | 18.8798 | 4.9855 | 13.2987 | 3.5797 | 18.8798 | 60
Shenakheda | 1941 | 5 | Monoblock | 4.646 | 20.6706 | 4.9448 | 19.0522 | 4.646 | 20.6706 | 58
Shenakheda | 116 | 15 | Monoblock | 3.8264 | 21.4337 | 4.4797 | 17.9602 | 3.8264 | 21.4337 | 58
Shenakheda | 129 | 7.5 | Monoblock | 3.96 | 18.9115 | 5.7991 | 12.6685 | 3.96 | 18.9115 | 60
Shenakheda | 2221 | 5 | Monoblock | 3.9312 | 24.4499 | 4.3974 | 21.4422 | 3.9312 | 24.4499 | 50
Shenakheda | 1948 | 5 | Monoblock | 4.8661 | 29.3446 | 4.9794 | 28.1319 | 4.8661 | 29.3446 | 56
Shenakheda | 127 | 7 | Monoblock | 5.1893 | 41.841 | 5.5828 | 38.1529 | 5.1893 | 41.841 | 56
Shenakheda | 884 | 5 | Monoblock | 3.8471 | 13.8739 | 4.6149 | 11.3459 | 3.8471 | 13.8739 | 56
Shenakheda | 789 | 7.5 | Monoblock | 3.8486 | 22.1675 | 7.1805 | 11.6555 | 3.8486 | 22.1675 | 56
Shenakheda | 2569 | 5 | Monoblock | 4.319 | 26.7221 | 5.0463 | 22.4364 | 4.319 | 26.7221 | 56
Shenakheda | New Connection | 5 | Monoblock | 4.2281 | 25 | 4.6049 | 22.5181 | 4.2281 | 25 | 56
Shenakheda | 651 | 7.5 | Monoblock | 4.4315 | 22.4944 | 4.8276 | 20.2563 | 4.4315 | 22.4944 | 56
Shenakheda | 580 | 5 | Monoblock | 4.471 | 22.7618 | 8.4173 | 11.8607 | 4.471 | 22.7618 | 56
Shenakheda | 4111 | 5 | Monoblock | 4.3208 | 26.3698 | 5.4306 | 20.5823 | 4.3208 | 26.3698 | 45
Shenakheda | 4107 | 5 | Monoblock | 4.8854 | 24.7525 | 4.8126 | 24.6495 | 4.8854 | 24.7525 | 50
Shenakheda | 2504 | 5 | Monoblock | 6.1254 | 29.7915 | 4.5845 | 39.0485 | 6.1254 | 29.7915 | 45
Shenakheda | 2496 | 5 | Monoblock | 6.4695 | 26.6588 | 4.9424 | 34.2332 | 6.4695 | 26.6588 | 45
Shenakheda | 2215 | 5 | Monoblock | 3.4074 | 12.2766 | 2.9393 | 13.9613 | 3.4074 | 12.2766 | 55
Shenakheda | 125 | 5 | Monoblock | 5.9516 | 28.4091 | 5.6486 | 29.3641 | 5.9516 | 28.4091 | 45
Shenakheda | 1944 | 5 | Monoblock | 5.8037 | 25.9067 | 3.0203 | 48.8354 | 5.8037 | 25.9067 | 45
Shenakheda | 1957 | 5 | Monoblock | 4.6398 | 15.5012 | 3.3887 | 20.8209 | 4.6398 | 15.5012 | 60
Shenakheda | 112 | 15 | Monoblock | 3.485 | 19.198 | 5.0645 | 12.9597 | 3.485 | 19.198 | 60
Shenakheda | New Connection |  | Monoblock | 4.0536 | 20.979 | 5.0513 | 16.5156 | 4.0536 | 20.979 | 58
Shenakheda | 2223 | 5 | Monoblock | 4.1055 | 27.3224 | 4.6348 | 23.7422 | 4.1055 | 27.3224 | 45
Shenakheda | 121 | 7.5 | Monoblock | 3.8873 | 24.43 | 3.4348 | 27.1233 | 3.8873 | 24.43 | 53
Shenakheda | 115 | 7.5 | Monoblock | 5.8381 | 31.5236 | 4.0842 | 44.2041 | 5.8381 | 31.5236 | 50
Shenakheda | 779 | 12.5 | Monoblock | 3.9357 | 27.5398 | 5.8556 | 18.1584 | 3.9357 | 27.5398 | 45
Shenakheda | 998 | 5 | Monoblock | 5.0913 | 15.6549 | 4.9716 | 15.7273 | 5.0913 | 15.6549 | 60
Shenakheda | 1943 | 5 | Monoblock | 5.4574 | 21.327 | 4.8972 | 23.3152 | 5.4574 | 21.327 | 58
Shenakheda | 1955 | 5 | Monoblock | 4.6673 | 19.2596 | 2.6531 | 33.2369 | 4.6673 | 19.2596 | 60
Shenakheda | 99 | 7.5 | Monoblock | 4.9021 | 24.43 | 4.1751 | 28.1389 | 4.9021 | 24.43 | 53
Shenakheda | New Connection | 5 | Monoblock | 5.4293 | 23.0828 | 3.097 | 39.697 | 5.4293 | 23.0828 | 53
Shenakheda | 2509 | 5 | Monoblock | 4.4127 | 22.7215 | 3.9844 | 24.6858 | 4.4127 | 22.7215 | 53
Shenakheda | 2511 | 5 | Monoblock | 5.8329 | 29.0323 | 6.2991 | 26.3728 | 5.8329 | 29.0323 | 45
Shenakheda | 2503 | 5 | Monoblock | 5.0613 | 23.8727 | 3.3301 | 35.594 | 5.0613 | 23.8727 | 53
Shenakheda | New Connection |  | Monoblock | 4.8293 | 25 | 3.7402 | 31.6667 | 4.8293 | 25 | 50
Shenakheda | New Connection |  | Monoblock | 3.5308 | 22.1566 | 3.2533 | 23.5895 | 3.5308 | 22.1566 | 56
Shenakheda | 2222 |  | Monoblock | 4.3281 | 19.5695 | 4.1009 | 20.2612 | 4.3281 | 19.5695 | 60
Shenakheda | New Connection |  | Monoblock | 5.3896 | 24.2457 | 3.6012 | 35.5974 | 5.3896 | 24.2457 | 53
Shenakheda | 1954 |  | Monoblock | 3.6017 | 25.4381 | 3.6388 | 24.7006 | 3.6017 | 25.4381 | 45
Shenakheda | 677 |  | Monoblock | 4.501 | 24.9307 | 6.2388 | 17.6446 | 4.501 | 24.9307 | 53
Shenakheda | 96 |  | Monoblock | 3.3361 | 28.2132 | 4.0371 | 22.8709 | 3.3361 | 28.2132 | 45
Shenakheda | 117 |  | Monoblock | 4.0955 | 33.9623 | 4.7383 | 28.7976 | 4.0955 | 33.9623 | 55
Shenakheda | 1942 |  | Monoblock | 4.8704 | 27.5229 | 4.7412 | 27.7357 | 4.8704 | 27.5229 | 45
Shenakheda | New Connection | 5 | Monoblock | 4.5436 | 17.5131 | 3.3961 | 22.9851 | 4.5436 | 17.5131 | 60
Shenakheda | New Connection | 5 | Monoblock | 4.4888 | 16.0456 | 3.4334 | 20.5792 | 4.4888 | 16.0456 | 60
Shenakheda | New Connection | 5 | Monoblock | 5.8807 | 27.881 | 5.3527 | 30.0491 | 5.8807 | 27.881 | 45
Shenakheda | 81 | 5 | Monoblock | 4.3107 | 19.5228 | 4.1523 | 19.8827 | 4.3107 | 19.5228 | 60
Shenakheda | 881 |  | Monoblock | 3.9244 | 24.2196 | 5.4305 | 17.1698 | 3.9244 | 24.2196 | 53
Shenakheda | 1194 | 5 | Monoblock | 3.4445 | 20.3114 | 4.6529 | 14.7508 | 3.4445 | 20.3114 | 60
Shenakheda | 856 | 7.5 | Monoblock | 4.5667 | 27.4223 | 2.8386 | 43.278 | 4.5667 | 27.4223 | 45
Shenakheda | 100 | 5 | Monoblock | 4.6004 | 18.5414 | 2.7178 | 30.7883 | 4.6004 | 18.5414 | 60
Shenakheda | 2558 | 5 | Monoblock | 4.9443 | 20.4918 | 3.536 | 28.1086 | 4.9443 | 20.4918 | 60
Shenakheda | 64 | 5 | Monoblock | 5.1174 | 24.6238 | 4.1143 | 30.0454 | 5.1174 | 24.6238 | 50
Shenakheda | 1200 | 5 | Monoblock | 4.8176 | 24.7389 | 3.4033 | 34.3547 | 4.8176 | 24.7389 | 50
Shenakheda | New Connection | 5 | Monoblock | 5.2089 | 19.4974 | 3.0127 | 33.0698 | 5.2089 | 19.4974 | 60
Shenakheda | 1026 | 5 | Monoblock | 4.9082 | 26.1097 | 6.5395 | 19.2242 | 4.9082 | 26.1097 | 45
Shenakheda | 2553 | 5 | Monoblock | 3.6989 | 23.7092 | 5.0026 | 17.1972 | 3.6989 | 23.7092 | 53
Shenakheda | 855 |  | Monoblock | 4.5714 | 28.8 | 4.6585 | 27.7243 | 4.5714 | 28.8 | 45
Shenakheda | 880 | 5 | Monoblock | 4.5717 | 18.8206 | 4.102 | 20.5769 | 4.5717 | 18.8206 | 60
Shenakheda | 102 | 5 | Monoblock | 5.504 | 31.9602 | 4.4169 | 39.0695 | 5.504 | 31.9602 | 55
Shenakheda | New Connection | 5 | Monoblock | 4.4711 | 24.1546 | 3.8653 | 27.4098 | 4.4711 | 24.1546 | 53
Shenakheda | 1195 | 5 | Monoblock | 5.6392 | 34.9108 | 4.5135 | 42.789 | 5.6392 | 34.9108 | 55
Shenakheda | 599 | 5 | Monoblock | 3.1795 | 21.7812 | 4.2716 | 15.9045 | 3.1795 | 21.7812 | 56
Shenakheda | 883 | 5 | Monoblock | 5.4616 | 27.281 | 2.8587 | 51.1296 | 5.4616 | 27.281 | 45
Shenakheda | 619 | 7.5 | Monoblock | 4.8957 | 30.2725 | 4.045 | 35.9426 | 4.8957 | 30.2725 | 50
Shenakheda | 97 | 5 | Monoblock | 5.0221 | 13.1791 | 5.387 | 12.0528 | 5.0221 | 13.1791 | 57
Shenakheda | 966 | 5 | Monoblock | 5.4146 | 25.1819 | 3.5761 | 37.4038 | 5.4146 | 25.1819 | 45
Shenakheda | 88 | 5 HP | Monoblock | 4.8381 | 25.59 | 4.799 | 25.3083 | 4.8381 | 25.59 | 45
Shenakheda | 68 | 12.5 | Monoblock | 4.7058 | 26.4395 | 3.5418 | 34.4611 | 4.7058 | 26.4395 | 45
Shenakheda | 1036 | 5 | Monoblock | 4.5186 | 28.5171 | 5.258 | 24.0416 | 4.5186 | 28.5171 | 45
Shenakheda | 1027 | 5 | Monoblock | 4.6478 | 24.7253 | 4.1668 | 27.056 | 4.6478 | 24.7253 | 50
Shenakheda | 747 | 5 | Monoblock | 4.2103 | 25.6776 | 4.9457 | 21.4439 | 4.2103 | 25.6776 | 45
Shenakheda | 1028 | 5 | Monoblock | 4.189 | 24.3112 | 3.3931 | 29.4438 | 4.189 | 24.3112 | 53
Shenakheda | New Connection | 5 | Monoblock | 4.9722 | 20.7708 | 4.6103 | 21.9759 | 4.9722 | 20.7708 | 58
Shenakheda | New Connection | 5 | Monoblock | 5.2183 | 26.0266 | 5.0795 | 26.2298 | 5.2183 | 26.0266 | 45
Shenakheda | 1186 | 5 | Monoblock | 5.4023 | 24.1676 | 4.5418 | 28.2004 | 5.4023 | 24.1676 | 53
Shenakheda | 49 | 5 | Monoblock | 4.9959 | 34.0136 | 5.2021 | 32.0446 | 4.9959 | 34.0136 | 55
Shenakheda | 620 | 5 | Monoblock | 4.7837 | 24.3375 | 7.539 | 15.1495 | 4.7837 | 24.3375 | 53
Shenakheda | 2001 | 5 | Monoblock | 4.894 | 30.3849 | 3.421 | 42.6411 | 4.894 | 30.3849 | 50
Shenakheda | 87 | 12.5 | Monoblock | 5.1803 | 32.3741 | 3.6814 | 44.6906 | 5.1803 | 32.3741 | 50
Shenakheda | 92 | 5 | Monoblock | 5.6879 | 24.0899 | 3.345 | 40.1851 | 5.6879 | 24.0899 | 53
Shenakheda | 93 | 7.5 | Monoblock | 4.6069 | 30.8219 | 3.3553 | 41.5149 | 4.6069 | 30.8219 | 50
Shenakheda | 902 |  | Monoblock | 5.3297 | 36.4964 | 5.0762 | 37.5905 | 5.3297 | 36.4964 | 45
Shenakheda | New Connection |  | Monoblock | 4.3669 | 20.7326 | 4.7105 | 18.855 | 4.3669 | 20.7326 | 58
Shenakheda | 2527 |  | Monoblock | 4.039 | 20.7469 | 3.3514 | 24.5285 | 4.039 | 20.7469 | 58
Shenakheda | 2573 |  | Submersible | 4.2636 | 18.572 | 4.23 | 18.3637 | 4.2636 | 18.572 | 60
Shenakheda | 2581 | 5 | Monoblock | 4.435 | 22.579 | 4.436 | 22.1449 | 4.435 | 22.579 | 53
Shenakheda | 1237 | 5 | Monoblock | 4.6587 | 19.6893 | 6.345 | 14.182 | 4.6587 | 19.6893 | 60
Shenakheda | 2545 | 5 | Monoblock | 3.6035 | 16.4354 | 4.0467 | 14.3572 | 3.6035 | 16.4354 | 60
Shenakheda | 101 |  | Monoblock | 4.2406 | 27.3723 | 3.9967 | 28.4905 | 4.2406 | 27.3723 | 45
Shenakheda | 2566 | 7.5 | Monoblock | 4.7169 | 24.3836 | 4.8786 | 23.1275 | 4.7169 | 24.3836 | 53
Shenakheda | 959 |  | Monoblock | 4.2773 | 26.0567 | 3.5374 | 30.9075 | 4.2773 | 26.0567 | 45
Shenakheda | 2561 | 7.5 | Monoblock | 4.2388 | 27.6243 | 3.1813 | 36.1078 | 4.2388 | 27.6243 | 45
Shenakheda | 514 |  | Monoblock | 4.3929 | 31.8359 | 2.8567 | 48.0251 | 4.3929 | 31.8359 | 50
Shenakheda | 78 | 5 | Monoblock | 5.329 | 21.7602 | 4.1907 | 27.1448 | 5.329 | 21.7602 | 56
Shenakheda | 2009 | 5 | Monoblock | 4.5053 | 24.7593 | 3.031 | 36.1033 | 4.5053 | 24.7593 | 50
Shenakheda | 634 | 5 | Monoblock | 4.442 | 22.3602 | 3.9133 | 24.8988 | 4.442 | 22.3602 | 56
Shenakheda | New Connection |  | Monoblock | 3.888 | 15.5226 | 3.9141 | 15.126 | 3.888 | 15.5226 | 60
Shenakheda | 3240 | 5 | Monoblock | 2.6332 | 32.4324 | 4.1633 | 20.1228 | 2.6332 | 32.4324 | 50
Shenakheda | 1023 | 5 | Monoblock | 3.0347 | 26.4784 | 4.3133 | 18.2754 | 3.0347 | 26.4784 | 45
Shenakheda | 696 | 5 | Monoblock | 3.2656 | 24.2131 | 5.0533 | 15.35 | 3.2656 | 24.2131 | 53
Shenakheda | New Connection |  | Monoblock | 3.8446 | 23.9425 | 3.6908 | 24.4666 | 3.8446 | 23.9425 | 53
Shenakheda | 930 | 5 | Monoblock | 4.3255 | 20.2384 | 3.8672 | 22.2066 | 4.3255 | 20.2384 | 60
Shenakheda | 983 | 5 | Monoblock | 5.5901 | 34.0136 | 4.8517 | 38.4457 | 5.5901 | 34.0136 | 55
Shenakheda | 2517 | 5 | Monoblock | 6.9452 | 23.7029 | 3.2354 | 49.9153 | 6.9452 | 23.7029 | 53
Shenakheda | 1197 | 5 | Monoblock | 4.9114 | 30.426 | 2.9634 | 49.4682 | 4.9114 | 30.426 | 50
Shenakheda | 937 | 5 | Monoblock | 5.1037 | 25.1607 | 5.0746 | 24.8244 | 5.1037 | 25.1607 | 45
Shenakheda | 1192 |  | Monoblock | 5.6571 | 22.6415 | 4.3052 | 29.1863 | 5.6571 | 22.6415 | 53
Shenakheda | 513 | 7.5 | Monoblock | 4.2831 | 41.8605 | 5.7686 | 30.4906 | 4.2831 | 41.8605 | 45
Shenakheda | 69 | 5 | Monoblock | 2.8496 | 24.5365 | 4.9269 | 13.9216 | 2.8496 | 24.5365 | 50
Shenakheda | 89 | 5 | Monoblock | 3.7689 | 26.738 | 5.7422 | 17.2162 | 3.7689 | 26.738 | 45
Shenakheda | 95 | 5 | Monoblock | 5.3006 | 21.6972 | 4.4816 | 25.1747 | 5.3006 | 21.6972 | 56
Shenakheda | 2528 | 5 | Monoblock | 4.2404 | 35.1562 | 4.6853 | 31.2137 | 4.2404 | 35.1562 | 45
Shenakheda | 4106 | 5 | Monoblock | 5.2493 | 20.2247 | 3.9738 | 26.2086 | 5.2493 | 20.2247 | 60
Shenakheda | 1183 | 5 | Monoblock | 3.6374 | 28.2132 | 5.2945 | 19.0145 | 3.6374 | 28.2132 | 45
Shenakheda | 2556 | 7.5 | Monoblock | 4.5696 | 40.9836 | 5.4082 | 33.9708 | 4.5696 | 40.9836 | 45
Shenakheda | 3171 | 5 | Monoblock | 4.5301 | 28.9762 | 3.9851 | 32.3134 | 4.5301 | 28.9762 | 45
Shenakheda | 2544 |  | Monoblock | 5.2159 | 27.6158 | 5.4813 | 25.7797 | 5.2159 | 27.6158 | 45
Shenakheda | 2586 | 5 | Monoblock | 5.4972 | 32.0856 | 3.5803 | 48.328 | 5.4972 | 32.0856 | 50
Shenakheda | New Connection | 5 | Monoblock | 4.1507 | 29.3542 | 5.2314 | 22.8476 | 4.1507 | 29.3542 | 45
Shenakheda | 2568 | 5 | Monoblock | 4.8348 | 32.1543 | 4.7952 | 31.8038 | 4.8348 | 32.1543 | 50
Shenakheda | New Connection | 5 | Monoblock | 5.0195 | 28.9296 | 4.6115 | 30.891 | 5.0195 | 28.9296 | 45
Shenakheda | New Connection | 7.5 | Monoblock | 3.6699 | 42.9799 | 5.6727 | 27.2774 | 3.6699 | 42.9799 | 45
Shenakheda | 2008 | 5 | Monoblock | 4.3591 | 28.5987 | 3.8447 | 31.8083 | 4.3591 | 28.5987 | 45
Shenakheda | 1198 | 5 | Monoblock | 3.5865 | 24.6643 | 3.3671 | 25.7725 | 3.5865 | 24.6643 | 50
Shenakheda | 2006 | 5 | Monoblock | 4.7278 | 29.1829 | 6.3095 | 21.4517 | 4.7278 | 29.1829 | 45
Shenakheda | New Connection | 5 | Monoblock | 4.3961 | 22.1239 | 5.3929 | 17.6917 | 4.3961 | 22.1239 | 56
Shenakheda | 2574 | 5 | Monoblock | 4.7857 | 24.3836 | 5.2465 | 21.8195 | 4.7857 | 24.3836 | 53
Shenakheda | 2010 | 5 | Monoblock | 3.0195 | 17.6574 | 6.2152 | 8.4154 | 3.0195 | 17.6574 | 60
Shenakheda | 2529 | 5 | Monoblock | 4.2801 | 25.9217 | 4.5365 | 23.9918 | 4.2801 | 25.9217 | 45
Shenakheda | 974 | 5 | Monoblock | 3.9696 | 24.5633 | 5.4805 | 17.4535 | 3.9696 | 24.5633 | 50
Shenakheda | 60 | 5 | Monoblock | 3.7425 | 27.5904 | 3.1762 | 31.8916 | 3.7425 | 27.5904 | 45
Shenakheda | 80 | 5 | Monoblock | 3.9236 | 24.4632 | 5.3307 | 17.6639 | 3.9236 | 24.4632 | 53
Shenakheda | 532 | 5 | Monoblock | 4.2305 | 25.1467 | 3.6965 | 28.2323 | 4.2305 | 25.1467 | 45
Shenakheda | 114 | 5 | Monoblock | 4.4596 | 34.3249 | 5.0458 | 29.7608 | 4.4596 | 34.3249 | 55
Shenakheda | 1214 | 5 | Monoblock | 3.9081 | 24.3046 | 5.1193 | 18.2019 | 3.9081 | 24.3046 | 53
Shenakheda | 1205 | 5 | Monoblock | 4.162 | 19.9291 | 3.0205 | 26.9392 | 4.162 | 19.9291 | 60
Shenakheda | 1215 | 5 | Monoblock | 3.7399 | 26.0191 | 5.7764 | 16.5258 | 3.7399 | 26.0191 | 45
Shenakheda | 534 | 5 | Monoblock | 4.6207 | 37.3444 | 6.1307 | 27.6118 | 4.6207 | 37.3444 | 45
Shenakheda | 61 | 5 | Monoblock | 5.9855 | 22.5225 | 3.9891 | 33.1522 | 5.9855 | 22.5225 | 53
Shenakheda | 105 | 5 | Monoblock | 2.9266 | 24.0513 | 5.5902 | 12.352 | 2.9266 | 24.0513 | 53
Shenakheda | 66 | 5 HP | Monoblock | 4.9035 | 13.3809 | 3.8749 | 16.6113 | 4.9035 | 13.3809 | 57
Shenakheda | 1226 | 5 | Monoblock | 4.6451 | 19.6121 | 5.1539 | 17.3404 | 4.6451 | 19.6121 | 60
Shenakheda | 1025 | 5 | Monoblock | 4.377 | 27.1739 | 4.8288 | 24.1632 | 4.377 | 27.1739 | 45
Shenakheda | New Connection | 10 | Monoblock | 4.5646 | 29.7915 | 6.9668 | 19.1483 | 4.5646 | 29.7915 | 45
Shenakheda | 67 | 7.5 | Monoblock | 4.3372 | 22.7043 | 6.0286 | 16.0241 | 4.3372 | 22.7043 | 53
Shenakheda | 587 | 7.5 | Monoblock | 6.0214 | 29.5664 | 7.0093 | 24.9168 | 6.0214 | 29.5664 | 45
Shenakheda | 3239 | 5 | Monoblock | 4.1266 | 31.8584 | 5.9736 | 21.59 | 4.1266 | 31.8584 | 50
Shenakheda | 949 | 5 | Monoblock | 4.3293 | 31.5568 | 5.9692 | 22.4527 | 4.3293 | 31.5568 | 50
Shenakheda | 630 | 5 | Monoblock | 4.8456 | 27.582 | 5.6879 | 23.051 | 4.8456 | 27.582 | 45
Shenakheda | 2528 | 5 | Monoblock | 4.4868 | 24.1481 | 10.6557 | 9.9749 | 4.4868 | 24.1481 | 53
Shenakheda | 875 | 5 | Monoblock | 2.4096 | 21.7549 | 3.2402 | 15.8709 | 2.4096 | 21.7549 | 56
Shenakheda | 1994 | 5 | Monoblock | 2.6225 | 22.9768 | 5.3206 | 11.1099 | 2.6225 | 22.9768 | 53
Shenakheda | 866 | 5 | Monoblock | 2.766 | 26.3312 | 4.7465 | 15.0528 | 2.766 | 26.3312 | 45
Shenakheda | 2014 | 5 | Monoblock | 3.4582 | 22.1293 | 5.2206 | 14.3801 | 3.4582 | 22.1293 | 56
Shenakheda | 63 | 5 | Monoblock | 4.6235 | 26.14 | 3.5729 | 33.1836 | 4.6235 | 26.14 | 45
Shenakheda | 1209 | 5 | Monoblock | 4.783 | 10.989 | 3.6982 | 13.9426 | 4.783 | 10.989 | 54
Shenakheda | 1042 | 5 | Monoblock | 4.3308 | 27.7949 | 4.7297 | 24.9672 | 4.3308 | 27.7949 | 45
Shenakheda | 730 | 5 | Monoblock | 3.8697 | 15.8284 | 3.4613 | 17.3598 | 3.8697 | 15.8284 | 60
Shenakheda | 743 | 5 | Monoblock | 3.3622 | 18.6877 | 6.8451 | 9.0048 | 3.3622 | 18.6877 | 60
Shenakheda | 82 | 5 | Monoblock | 4.5403 | 25.1607 | 3.6577 | 30.6391 | 4.5403 | 25.1607 | 45
Shenakheda | 1201 | 5 | Monoblock | 3.8657 | 23.8854 | 3.4712 | 26.0949 | 3.8657 | 23.8854 | 53
Shenakheda | New Connection | 5 | Monoblock | 4.6478 | 32.7035 | 5.9651 | 24.9973 | 4.6478 | 32.7035 | 50
Shenakheda | 1208 | 5 | Monoblock | 3.1029 | 20.8092 | 3.2451 | 19.5196 | 3.1029 | 20.8092 | 58
Shenakheda | 1021 | 5 | Monoblock | 4.0437 | 21.0379 | 4.7492 | 17.5724 | 4.0437 | 21.0379 | 58
Shenakheda | 2543 | 5 | Monoblock | 4.1105 | 26.5252 | 3.0122 | 35.5082 | 4.1105 | 26.5252 | 45
Shenakheda | 2000 | 5 | Monoblock | 3.6462 | 18.1928 | 3.4976 | 18.6054 | 3.6462 | 18.1928 | 60
Shenakheda | 631 | 5 | Monoblock | 3.7349 | 15.4985 | 5.3111 | 10.6918 | 3.7349 | 15.4985 | 60
Shenakheda | 3246 | 5 | Monoblock | 4.4729 | 30.9598 | 6.0213 | 22.5617 | 4.4729 | 30.9598 | 50
Shenakheda | 3247 | 5 | Monoblock | 4.955 | 24.1222 | 4.7919 | 24.4694 | 4.955 | 24.1222 | 53
Shenakheda | 3245 | 5 | Monoblock | 4.7892 | 26.1248 | 6.3504 | 19.3278 | 4.7892 | 26.1248 | 45
Shenakheda | 3249 | 5 | Monoblock | 3.8183 | 12.6814 | 4.8204 | 9.8543 | 3.8183 | 12.6814 | 57
Shenakheda | 62 | 20 | Monoblock | 3.7866 | 21.8129 | 5.2947 | 15.3034 | 3.7866 | 21.8129 | 56
Shenakheda | 548 | 10 | Monoblock | 4.984 | 28.4091 | 6.0138 | 23.0969 | 4.984 | 28.4091 | 45
Shenakheda | 1223 | 5 | Monoblock | 4.1247 | 18.3486 | 4.2301 | 17.5516 | 4.1247 | 18.3486 | 60
Shenakheda | 1204 | 5 | Monoblock | 4.3701 | 33.1492 | 4.978 | 28.5482 | 4.3701 | 33.1492 | 55
Shenakheda | 1222 | 5 | Monoblock | 4.1106 | 36.2319 | 5.5193 | 26.4717 | 4.1106 | 36.2319 | 45
Shenakheda | 1043 | 5 | Monoblock | 4.2948 | 35.9138 | 6.3741 | 23.7387 | 4.2948 | 35.9138 | 45
Shenakheda | 1039 | 5 | Monoblock | 3.3774 | 19.1327 | 3.417 | 18.5514 | 3.3774 | 19.1327 | 60
Shenakheda | 79 | 7.5 | Monoblock | 3.8789 | 23.1541 | 4.6619 | 18.8992 | 3.8789 | 23.1541 | 53
Shenakheda | 1029 | 5 | Monoblock | 4.0354 | 22.5451 | 4.7756 | 18.6888 | 4.0354 | 22.5451 | 53
Shenakheda | 1225 | 5 | Monoblock | 2.7641 | 19.0315 | 3.2717 | 15.7733 | 2.7641 | 19.0315 | 60
Shenakheda | 3261 | 5 | Monoblock | 4.2997 | 18.9274 | 2.531 | 31.5434 | 4.2997 | 18.9274 | 60
Shenakheda | 1203 | 5 | Monoblock | 3.4082 | 23.879 | 4.4118 | 18.0962 | 3.4082 | 23.879 | 53
Shenakheda | 1995 | 5 | Monoblock | 3.1334 | 28.0287 | 3.7563 | 22.9366 | 3.1334 | 28.0287 | 45
Shenakheda | 1996 | 5 | Monoblock | 4.1507 | 24.3638 | 5.707 | 17.383 | 4.1507 | 24.3638 | 53
Shenakheda | 1188 | 5 | Monoblock | 4.2042 | 24.4698 | 4.7554 | 21.2225 | 4.2042 | 24.4698 | 53
Shenakheda | 825 | 5 | Monoblock | 2.8171 | 20.4453 | 4.204 | 13.4401 | 2.8171 | 20.4453 | 60
Shenakheda | 1997 | 5 | Monoblock | 3.1812 | 27.7179 | 4.1392 | 20.8981 | 3.1812 | 27.7179 | 45
Shenakheda | 70 | 5 | Monoblock | 4.0947 | 26.4162 | 5.0438 | 21.0377 | 4.0947 | 26.4162 | 45
Shenakheda | 1202 | 5 | Monoblock | 3.0958 | 20.9497 | 4.5977 | 13.8379 | 3.0958 | 20.9497 | 58
Shenakheda | 2557 | 5 | Monoblock | 5.5441 | 26.8336 | 4.7285 | 30.8642 | 5.5441 | 26.8336 | 45
Shenakheda | New Connection | 5 | Monoblock | 3.7476 | 20.339 | 3.5961 | 20.7934 | 3.7476 | 20.339 | 60
Shenakheda | New Connection | 5 | Monoblock | 6.4354 | 46.8994 | 7.618 | 38.866 | 6.4354 | 46.8994 | 61
Shenakheda | 3243 | 5 | Monoblock | 5.8754 | 32.0171 | 5.6735 | 32.5265 | 5.8754 | 32.0171 | 50
Shenakheda | 65 | 5 | Monoblock | 5.9304 | 31.6233 | 8.1117 | 22.6801 | 5.9304 | 31.6233 | 55
Shenakheda | 3255 | 5 | Monoblock | 3.7152 | 26.5487 | 5.8777 | 16.4621 | 3.7152 | 26.5487 | 45
Shenakheda | 3257 | 5 | Monoblock | 4.6758 | 20.6849 | 3.0314 | 31.2991 | 4.6758 | 20.6849 | 58
Shenakheda | 1227 | 5 | Monoblock | 4.7373 | 19.2885 | 3.0739 | 29.1614 | 4.7373 | 19.2885 | 60
Shenakheda | 533 | 5 | Monoblock | 5.6704 | 31.9602 | 5.8776 | 30.248 | 5.6704 | 31.9602 | 55
Shenakheda | 3252 | 5 | Monoblock | 4.4205 | 18.2852 | 4.2887 | 18.4891 | 4.4205 | 18.2852 | 60
Shenakheda | 1218 | 5 | Monoblock | 4.9744 | 16.3399 | 2.5901 | 30.7847 | 4.9744 | 16.3399 | 60
Shenakheda | 1219 | 5 | Monoblock | 4.3709 | 17.0519 | 4.311 | 16.9604 | 4.3709 | 17.0519 | 60
Shenakheda | New Connection | 5 | Monoblock | 4.1018 | 20.6992 | 6.0668 | 13.729 | 4.1018 | 20.6992 | 58
Shenakheda | 1212 | 5 | Monoblock | 4.4592 | 29.4214 | 4.7163 | 27.289 | 4.4592 | 29.4214 | 45
Shenakheda | New Connection | 5 | Monoblock | 3.4207 | 8.7762 | 3.0665 | 9.6039 | 3.4207 | 8.7762 | 50
Shenakheda | 1220 | 5 | Monoblock | 4.4993 | 29.7128 | 5.3599 | 24.4681 | 4.4993 | 29.7128 | 45
Shenakheda | 3248 | 5 | Monoblock | 4.6086 | 26.2161 | 4.2816 | 27.682 | 4.6086 | 26.2161 | 45
Shenakheda | 1206 | 5 | Monoblock | 5.4352 | 24.7253 | 4.0268 | 32.7388 | 5.4352 | 24.7253 | 50
Shenakheda | 629 | 5 | Monoblock | 5.3597 | 27.5735 | 4.2171 | 34.3791 | 5.3597 | 27.5735 | 45
Shenakheda | 1221 | 5 | Monoblock | 5.2746 | 21.1815 | 4.4059 | 24.8759 | 5.2746 | 21.1815 | 58
Shenakheda | 2547 | 5 | Monoblock | 4.6075 | 30.6958 | 6.6569 | 20.842 | 4.6075 | 30.6958 | 50
Shenakheda | 2548 | 5 | Monoblock | 5.1576 | 29.1262 | 6.3032 | 23.3795 | 5.1576 | 29.1262 | 45
Shenakheda | New Connection | 5 | Monoblock | 5.1228 | 16.266 | 4.4063 | 18.5518 | 5.1228 | 16.266 | 60
Shenakheda | 1038 | 5 | Monoblock | 3.8476 | 22.7733 | 5.6669 | 15.1682 | 3.8476 | 22.7733 | 53
Shenakheda | New Connection | 5 | Monoblock | 4.0885 | 27.7778 | 3.6639 | 30.4077 | 4.0885 | 27.7778 | 45
Shenakheda | 3250 | 5 | Monoblock | 4.9006 | 25.7658 | 5.9727 | 20.7391 | 4.9006 | 25.7658 | 45
Shenakheda | New Connection | 5 | Monoblock | 4.1088 | 29.6932 | 2.8266 | 42.3426 | 4.1088 | 29.6932 | 45
Shenakheda | 1033 | 5 | Monoblock | 3.664 | 18.0505 | 3.5959 | 18.0427 | 3.664 | 18.0505 | 60
Shenakheda | 1034 | 5 | Monoblock | 3.9354 | 17.4317 | 3.6615 | 18.3798 | 3.9354 | 17.4317 | 60
Shenakheda | 954 | 5 | Monoblock | 4.7424 | 35.5731 | 5.432 | 30.4669 | 4.7424 | 35.5731 | 45
Shenakheda | 1037 | 5 | Monoblock | 4.1201 | 23.0297 | 4.011 | 23.2065 | 4.1201 | 23.0297 | 53
Shenakheda | 1031 | 5 | Monoblock | 3.9672 | 26.3466 | 3.3359 | 30.7369 | 3.9672 | 26.3466 | 45
Shenakheda | 1199 | 5 | Monoblock | 4.4496 | 22.2772 | 5.889 | 16.5126 | 4.4496 | 22.2772 | 56
Shenakheda | 3253 | 5 | Monoblock | 4.1345 | 27.3058 | 3.8139 | 29.0386 | 4.1345 | 27.3058 | 45
Shenakheda | 84 | 5 | Monoblock | 3.9734 | 23.5479 | 3.6983 | 24.8193 | 3.9734 | 23.5479 | 53
Shenakheda | New Connection | 5 | Monoblock | 4.9008 | 18.8206 | 6.0211 | 15.0276 | 4.9008 | 18.8206 | 60
Shenakheda | New Connection | 5 | Monoblock | 4.8812 | 25.4597 | 4.7659 | 25.5798 | 4.8812 | 25.4597 | 45
Shenakheda | 609 | 5 | Monoblock | 5.3349 | 30.654 | 6.7867 | 23.6388 | 5.3349 | 30.654 | 50
Shenakheda | 108 | 5 | Monoblock | 5.0742 | 27.1903 | 6.0236 | 22.4698 | 5.0742 | 27.1903 | 45
Shenakheda | 976 | 5 | Monoblock | 4.3997 | 28.0987 | 5.5589 | 21.8166 | 4.3997 | 28.0987 | 45
Shenakheda | 878 | 5 | Monoblock | 4.9287 | 27.6583 | 4.7235 | 28.3119 | 4.9287 | 27.6583 | 45
Shenakheda | 2559 | 5 | Monoblock | 4.9799 | 28.3733 | 6.2419 | 22.2063 | 4.9799 | 28.3733 | 45
Shenakheda | 3259 | 5 | Monoblock | 4.0458 | 20.7708 | 6.5246 | 12.6348 | 4.0458 | 20.7708 | 58
Shenakheda | 3254 | 5 | Monoblock | 3.9077 | 16.4114 | 4.6168 | 13.6267 | 3.9077 | 16.4114 | 60
Shenakheda | 2515 | 5 | Monoblock | 3.5469 | 14.245 | 3.0635 | 16.1796 | 3.5469 | 14.245 | 58
Shenakheda | 3258 | 5 | Monoblock | 4.5023 | 24.3178 | 3.6007 | 29.829 | 4.5023 | 24.3178 | 53
Shenakheda | New Connection | 5 | Monoblock | 3.5977 | 24.5432 | 3.5058 | 24.7081 | 3.5977 | 24.5432 | 50
Shenakheda | 2552 | 5 | Monoblock | 4.1482 | 23.9107 | 4.6635 | 20.8645 | 4.1482 | 23.9107 | 53
Shenakheda | 810 | 5 | Monoblock | 4.2918 | 27.1903 | 3.8664 | 29.6081 | 4.2918 | 27.1903 | 45
Shenakheda | 2534 | 5 | Monoblock | 4.2262 | 24.7729 | 3.3631 | 30.5388 | 4.2262 | 24.7729 | 50
Shenakheda | New Connection | 5 | Monoblock | 4.042 | 27.6923 | 4.2442 | 25.8717 | 4.042 | 27.6923 | 45
Shenakheda | New Connection | 5 | Monoblock | 4.2099 | 30.8854 | 5.2299 | 24.3891 | 4.2099 | 30.8854 | 50
Shenakheda | New Connection | 5 | Monoblock | 4.9387 | 27.9764 | 6.3532 | 21.3342 | 4.9387 | 27.9764 | 45
Shenakheda | New Connection | 5 | Monoblock | 5.0947 | 27.3723 | 4.7403 | 28.86 | 5.0947 | 27.3723 | 45
Shenakheda | 873 | 5 | Monoblock | 3.5701 | 23.5664 | 4.8415 | 17.0476 | 3.5701 | 23.5664 | 53
Shenakheda | New Connection | 5 | Monoblock | 3.7517 | 20.1568 | 4.2346 | 17.5192 | 3.7517 | 20.1568 | 60
Shenakheda | 106 | 5 | Monoblock | 4.058 | 19.9159 | 3.967 | 19.9856 | 4.058 | 19.9159 | 60
Shenakheda | 759 | 5 | Monoblock | 5.2659 | 14.6246 | 4.1574 | 18.1721 | 5.2659 | 14.6246 | 58
Shenakheda | 628 | 5 | Monoblock | 3.8553 | 6.9003 | 2.7887 | 9.3584 | 3.8553 | 6.9003 | 45
Shenakheda | 656 | 5 | Monoblock | 4.7479 | 26.14 | 5.7474 | 21.184 | 4.7479 | 26.14 | 45
Shenakheda | 2531 | 5 | Monoblock | 4.0841 | 28.5261 | 4.4917 | 25.4445 | 4.0841 | 28.5261 | 45
Shenakheda | 1193 | 5 | Monoblock | 3.3576 | 26.5565 | 4.0412 | 21.6451 | 3.3576 | 26.5565 | 45
Shenakheda | 650 | 5 | Monoblock | 3.8027 | 23.0828 | 4.7029 | 18.3099 | 3.8027 | 23.0828 | 53
Shenakheda | 2575 | 5 | Monoblock | 4.4066 | 22.5677 | 4.1699 | 23.3959 | 4.4066 | 22.5677 | 53
Shenakheda | 2533 | 5 | Monoblock | 4.4688 | 31.2609 | 5.22 | 26.2538 | 4.4688 | 31.2609 | 56
Shenakheda | 2576 | 5 | Monoblock | 4.0789 | 21.6398 | 7.1281 | 12.1475 | 4.0789 | 21.6398 | 56
Shenakheda | 2532 | 5 | Monoblock | 3.8144 | 24.1805 | 2.881 | 31.4063 | 3.8144 | 24.1805 | 53
Shenakheda | 2539 | 5 | Monoblock | 5.2329 | 26.9058 | 3.6036 | 38.3281 | 5.2329 | 26.9058 | 45
Shenakheda | 510 | 5 | Monoblock | 4.7832 | 24.3243 | 6.0433 | 18.8866 | 4.7832 | 24.3243 | 53
Shenakheda | 2578 | 5 | Monoblock | 3.6679 | 18.711 | 4.7871 | 14.064 | 3.6679 | 18.711 | 60
Shenakheda | New Connection | 5 | Monoblock | 4.6091 | 27.027 | 4.2128 | 29.0076 | 4.6091 | 27.027 | 45
Shenakheda | 2540 | 5 | Monoblock | 4.4702 | 30.303 | 3.2055 | 41.4556 | 4.4702 | 30.303 | 50
Shenakheda | 2536 | 5 | Monoblock | 4.6744 | 21.7759 | 4.0681 | 24.5462 | 4.6744 | 21.7759 | 56
Shenakheda | 1980 | 5 | Monoblock | 2.9753 | 16.4384 | 4.1987 | 11.4273 | 2.9753 | 16.4384 | 60
Shenakheda | 3208 | 5 | Monoblock | 7.5109 | 23.2198 | 3.9313 | 43.5201 | 7.5109 | 23.2198 | 53
Shenakheda | 3226 | 5 | Monoblock | 7.4098 | 20.7326 | 3.3985 | 44.3446 | 7.4098 | 20.7326 | 58
Shenakheda | 3207 | 5 | Monoblock | 7.5514 | 24.5098 | 3.4996 | 51.8822 | 7.5514 | 24.5098 | 50
Shenakheda | 3206 | 5 | Monoblock | 6.8056 | 20.8768 | 9.2036 | 15.144 | 6.8056 | 20.8768 | 58
Shenakheda | 3167 | 5 | Monoblock | 6.4157 | 26.3466 | 5.9214 | 28.0036 | 6.4157 | 26.3466 | 45
Shenakheda | 3168 | 5 | Monoblock | 5.7209 | 25.0627 | 6.0875 | 23.1061 | 5.7209 | 25.0627 | 45
Shenakheda | 3179 | 5 | Monoblock | 6.3657 | 24.8894 | 5.2953 | 29.352 | 6.3657 | 24.8894 | 50
Shenakheda | 1979 | 5 | Monoblock | 5.1669 | 24.6171 | 4.3476 | 28.7004 | 5.1669 | 24.6171 | 50
Shenakheda | 3188 | 5 | Monoblock | 3.7502 | 21.5157 | 4.2045 | 18.826 | 3.7502 | 21.5157 | 56
Shenakheda | 1870 | 5 | Monoblock | 4.5941 | 19.3507 | 4.097 | 21.2866 | 4.5941 | 19.3507 | 60
Shenakheda | 58 | 5 | Monoblock | 4.6253 | 19.5016 | 4.8714 | 18.1646 | 4.6253 | 19.5016 | 60
Shenakheda | 3216 | 5 | Monoblock | 4.4935 | 16.2162 | 3.348 | 21.3512 | 4.4935 | 16.2162 | 60
Shenakheda | 1984 | 5 | Monoblock | 4.1926 | 24.7729 | 3.9232 | 25.9706 | 4.1926 | 24.7729 | 50
Shenakheda | 3170 | 5 | Monoblock | 4.9503 | 20.6564 | 6.1841 | 16.2211 | 4.9503 | 20.6564 | 58
Shenakheda | 57 | 5 | Monoblock | 4.473 | 24.2001 | 3.9398 | 26.9534 | 4.473 | 24.2001 | 53
Shenakheda | 3234 | 5 | Monoblock | 4.1626 | 30.2521 | 4.2608 | 28.993 | 4.1626 | 30.2521 | 50
Shenakheda | 3233 | 5 | Monoblock | 4.4197 | 22.3769 | 5.6984 | 17.026 | 4.4197 | 22.3769 | 56
Shenakheda | 1983 | 5 | Monoblock | 4.5166 | 24.6373 | 3.8012 | 28.7175 | 4.5166 | 24.6373 | 50
Shenakheda | 1982 | 5 | Monoblock | 4.9818 | 20.5667 | 2.8565 | 35.1879 | 4.9818 | 20.5667 | 58
Shenakheda | 3157 | 5 | Monoblock | 4.279 | 27.133 | 4.1943 | 27.1552 | 4.279 | 27.133 | 45
Shenakheda | 1862 | 5 | Monoblock | 5.994 | 30.2928 | 5.9405 | 29.9849 | 5.994 | 30.2928 | 50
Shenakheda | New Connection | 5 | Monoblock | 5.2605 | 20.9644 | 3.8087 | 28.4051 | 5.2605 | 20.9644 | 58
Shenakheda | 1864 | 5 | Monoblock | 5.2043 | 36.9004 | 4.5657 | 41.262 | 5.2043 | 36.9004 | 45
Shenakheda | 1859 | 5 | Monoblock | 3.628 | 17.616 | 4.3081 | 14.5528 | 3.628 | 17.616 | 60
Shenakheda | 3230 | 5 | Monoblock | 3.5846 | 16.0399 | 4.0886 | 13.7955 | 3.5846 | 16.0399 | 60
Shenakheda | New Connection | 5 | Monoblock | 2.8984 | 18.5644 | 4.0192 | 13.1332 | 2.8984 | 18.5644 | 60
Shenakheda | 51 | 5 | Monoblock | 3.0745 | 13.8782 | 3.2449 | 12.8994 | 3.0745 | 13.8782 | 58
Shenakheda | 1868 | 5 | Monoblock | 3.3088 | 16.9555 | 3.479 | 15.8195 | 3.3088 | 16.9555 | 60
Shenakheda | 1867 | 5 | Monoblock | 4.6437 | 32.5145 | 4.1405 | 35.7729 | 4.6437 | 32.5145 | 50
Shenakheda | 3189 | 5 | Monoblock | 3.9839 | 31.679 | 3.6295 | 34.1114 | 3.9839 | 31.679 | 50
Shenakheda | 3228 | 5 | Monoblock | 3.3874 | 19.3507 | 4.4024 | 14.6066 | 3.3874 | 19.3507 | 60
Shenakheda | 3178 | 5 | Monoblock | 4.7117 | 18.0036 | 4.3426 | 19.1624 | 4.7117 | 18.0036 | 60
Shenakheda | 3176 | 5 | Monoblock | 5.0148 | 21.85 | 4.8477 | 22.1735 | 5.0148 | 21.85 | 56
Shenakheda | 3227 | 5 | Monoblock | 2.9371 | 19.1898 | 6.0135 | 9.1947 | 2.9371 | 19.1898 | 60
Shenakheda | 3215 | 5 | Monoblock | 4.4142 | 21.8341 | 5.1547 | 18.3421 | 4.4142 | 21.8341 | 56
Shenakheda | 3183 | 5 | Monoblock | 3.2786 | 16.4474 | 3.4234 | 15.4527 | 3.2786 | 16.4474 | 60
Shenakheda | 3204 | 5 | Monoblock | 4.1038 | 25.7069 | 5.0778 | 20.3812 | 4.1038 | 25.7069 | 45
Shenakheda | 1858 | 5 | Monoblock | 3.9461 | 21.9727 | 4.1587 | 20.4529 | 3.9461 | 21.9727 | 56
Shenakheda | 3192 | 5 | Monoblock | 2.8443 | 10.577 | 3.2982 | 8.9481 | 2.8443 | 10.577 | 54
Shenakheda | 3229 | 5 | Monoblock | 3.1166 | 15.4295 | 3.5846 | 13.16 | 3.1166 | 15.4295 | 58
Shenakheda | AP/3182 | 5 | Monoblock | 4.7565 | 22.6415 | 4.7011 | 22.4729 | 4.7565 | 22.6415 | 53
Shenakheda | AP/59 | 10 | Monoblock | 5.0004 | 28.1338 | 5.2893 | 26.0921 | 5.0004 | 28.1338 | 45
Shenakheda | AP/3194 | 5 | Monoblock | 4.4288 | 23.31 | 5.8447 | 17.3275 | 4.4288 | 23.31 | 53
Shenakheda | AP/1985 | 5 | Monoblock | 4.4616 | 14.4555 | 3.1304 | 20.2111 | 4.4616 | 14.4555 | 58
Shenakheda | AP/846 | 5 | Monoblock | 4.9368 | 19.8282 | 3.0787 | 31.1915 | 4.9368 | 19.8282 | 60
Shenakheda | AP/1981 | 5 | Monoblock | 4.3187 | 19.3133 | 4.8695 | 16.8032 | 4.3187 | 19.3133 | 60
Shenakheda | AP/1866 | 5 | Monoblock | 3.8831 | 23.9234 | 3.3912 | 26.8724 | 3.8831 | 23.9234 | 53
Shenakheda | AP/1865 | 5 | Monoblock | 5.9604 | 23.5973 | 4.0983 | 33.6672 | 5.9604 | 23.5973 | 53
Shenakheda | AP/847 | 5 | Monoblock | 4.1868 | 23.898 | 3.4342 | 28.5813 | 4.1868 | 23.898 | 53
Shenakheda | AP/1861 | 5 | Monoblock | 3.8661 | 22.2552 | 3.5357 | 23.8723 | 3.8661 | 22.2552 | 56
Shenakheda | 3235 | 5 | Monoblock | 4.1993 | 23.8284 | 5.3217 | 18.4455 | 4.1993 | 23.8284 | 53
Shenakheda | 3172 | 5 | Monoblock | 4.2189 | 24.0835 | 4.5793 | 21.7662 | 4.2189 | 24.0835 | 53
Shenakheda | New Connection | 5 | Monoblock | 4.0264 | 24.077 | 6.1086 | 15.5685 | 4.0264 | 24.077 | 53
Shenakheda | 3200 | 5 | Monoblock | 5.3819 | 34.4432 | 4.7838 | 38.0134 | 5.3819 | 34.4432 | 55
Shenakheda | 3201 | 5 | Monoblock | 4.5518 | 24.855 | 4.852 | 22.8742 | 4.5518 | 24.855 | 53
Shenakheda | 3222 | 5 | Monoblock | 4.019 | 20.0401 | 4.6488 | 16.9961 | 4.019 | 20.0401 | 60
Shenakheda | 3238 | 5 | Monoblock | 4.3102 | 19.3632 | 4.9188 | 16.6449 | 4.3102 | 19.3632 | 60
Shenakheda | 3223 | 5 | Monoblock | 4.0375 | 15.7673 | 3.4116 | 18.3059 | 4.0375 | 15.7673 | 60
Shenakheda | 3186 | 5 | Monoblock | 4.1064 | 22.0049 | 3.6027 | 24.6049 | 4.1064 | 22.0049 | 56
Shenakheda | New Connection | 5 | Monoblock | 4.3704 | 20.8237 | 3.8148 | 23.4037 | 4.3704 | 20.8237 | 58
Shenakheda | 3160 | 5 | Monoblock | 5.4048 | 24.2261 | 3.4664 | 37.0556 | 5.4048 | 24.2261 | 53
Shenakheda | 3236 | 5 | Monoblock | 4.9481 | 19.8413 | 4.1298 | 23.3208 | 4.9481 | 19.8413 | 60
Shenakheda | 1987 | 5 | Monoblock | 4.256 | 25.6046 | 4.4416 | 24.0685 | 4.256 | 25.6046 | 45
Shenakheda | New Connection | 5 | Monoblock | 4.2921 | 19.1367 | 5.244 | 15.3654 | 4.2921 | 19.1367 | 60
Shenakheda | 817 | 10 | Monoblock | 4.6607 | 26.8657 | 5.3279 | 23.0546 | 4.6607 | 26.8657 | 45
Shenakheda | 2241 | 5 | Monoblock | 4.6178 | 18.5033 | 4.1874 | 20.0173 | 4.6178 | 18.5033 | 60
Shenakheda | 2228 | 5 | Monoblock | 4.4948 | 23.622 | 4.7228 | 22.0549 | 4.4948 | 23.622 | 53
Shenakheda | 1740 | 5 | Monoblock | 2.8529 | 21.6398 | 6.2412 | 9.7039 | 2.8529 | 21.6398 | 56
Shenakheda | 2381 | 5 | Monoblock | 3.2199 | 29.7226 | 3.6164 | 25.9607 | 3.2199 | 29.7226 | 45
Shenakheda | New Connection |  | Monoblock | 2.7902 | 20.4128 | 5.0227 | 11.1243 | 2.7902 | 20.4128 | 60
Shenakheda | New Connection | 5 | Monoblock | 3.3652 | 19.3757 | 4.9141 | 13.0164 | 3.3652 | 19.3757 | 60
Shenakheda | New Connection | 10 | Monoblock | 3.5586 | 29.9003 | 6.8961 | 15.1365 | 3.5586 | 29.9003 | 45
Shenakheda | New Connection | 5 | Monoblock | 2.4307 | 17.9069 | 3.8972 | 10.9565 | 2.4307 | 17.9069 | 60
Shenakheda | New Connection | 5 | Monoblock | 2.3414 | 24.0706 | 2.868 | 19.2774 | 2.3414 | 24.0706 | 53
Shenakheda | New Connection | 5 | Monoblock | 2.437 | 18.2297 | 4.7908 | 9.097 | 2.437 | 18.2297 | 60
Shenakheda | 1163 | 5 | Monoblock | 4.4406 | 18.5338 | 3.4137 | 23.6511 | 4.4406 | 18.5338 | 60
Shenakheda | 1143 | 5 | Monoblock | 2.7274 | 25.1397 | 6.0219 | 11.1697 | 2.7274 | 25.1397 | 45
Shenakheda | 3289 | 5 | Monoblock | 2.4992 | 15.2181 | 3.9166 | 9.5262 | 2.4992 | 15.2181 | 58
Shenakheda | 891 |  | Monoblock | 3.341 | 12.7732 | 3.8009 | 11.0144 | 3.341 | 12.7732 | 57
Shenakheda | 2384 | 5 | Monoblock | 3.8251 | 13.8334 | 3.1044 | 16.721 | 3.8251 | 13.8334 | 58
Shenakheda | 1652 | 5 | Monoblock | 3.5845 | 22.4607 | 5.1199 | 15.4262 | 3.5845 | 22.4607 | 56
Shenakheda | New Connection | 5 | Monoblock | 2.2954 | 22.965 | 5.0429 | 10.2546 | 2.2954 | 22.965 | 53
Shenakheda | 2398 | 5 | Monoblock | 4.5672 | 18.68 | 5.8623 | 14.2766 | 4.5672 | 18.68 | 60
Shenakheda | 1737 | 5 | Monoblock | 4.4532 | 23.3584 | 4.323 | 23.6045 | 4.4532 | 23.3584 | 53
Shenakheda | 143 | 5 | Monoblock | 3.5752 | 24.9931 | 5.6133 | 15.6163 | 3.5752 | 24.9931 | 50
Shenakheda | 868 | 5 | Monoblock | 2.6681 | 24.4831 | 5.891 | 10.8779 | 2.6681 | 24.4831 | 53
Shenakheda | 1168 | 5 | Monoblock | 5.8675 | 19.8238 | 4.3869 | 26.0101 | 5.8675 | 19.8238 | 60
Shenakheda | 2384 | 5 | Monoblock | 3.9756 | 26.1248 | 5.6563 | 18.0134 | 3.9756 | 26.1248 | 45
Shenakheda | 1700 | 5 | Monoblock | 3.5836 | 16.5168 | 3.8052 | 15.2593 | 3.5836 | 16.5168 | 60
Shenakheda | 2389 | 5 | Monoblock | 3.2714 | 16.2514 | 2.9657 | 17.586 | 3.2714 | 16.2514 | 60
Shenakheda | 1751 | 5 | Monoblock | 3.217 | 21.1069 | 3.9414 | 16.9004 | 3.217 | 21.1069 | 58
Shenakheda | 892 | 5 | Monoblock | 3.0281 | 18.3636 | 4.5758 | 11.9216 | 3.0281 | 18.3636 | 60
Shenakheda | 3251 | 5 | Monoblock | 4.5925 | 18.3187 | 4.9072 | 16.818 | 4.5925 | 18.3187 | 50
Shenakheda | 2390 | 5 | Monoblock | 2.3182 | 23.3402 | 4.0756 | 13.0238 | 2.3182 | 23.3402 | 60
Shenakheda | 2513 |  | Monoblock | 4.7201 | 29.2588 | 5.0791 | 26.674 | 4.7201 | 29.2588 | 53
Shenakheda | 2555 | 5 | Monoblock | 3.3971 | 19.698 | 4.531 | 14.4876 | 3.3971 | 19.698 | 60
Shenakheda | 122 | 5 | Monoblock | 4.8509 | 24.5566 | 4.5874 | 25.4736 | 4.8509 | 24.5566 | 50
Shenakheda | 76 | 5 | Monoblock | 7.6205 | 24.9169 | 4.8147 | 38.6883 | 7.6205 | 24.9169 | 50
Shenakheda | 896 | 5 | Monoblock | 3.9436 | 17.301 | 3.6 | 18.5924 | 3.9436 | 17.301 | 60
Shenakheda | 3284 | 5 | Monoblock | 4.2107 | 27.5989 | 5.7878 | 19.697 | 4.2107 | 27.5989 | 45
Shenakheda | 437 | 5 | Monoblock | 4.4426 | 28.9017 | 4.3267 | 29.112 | 4.4426 | 28.9017 | 45

## Punjawa
Feeder Name | Account No. | Connected HP / Sanctioned Demand | Type of Pump | Existing Pump Set Measured Parameters |  |  |  | Energy Efficient Pump Sets Parameters
|  |  |  | Total Head (m) | Flow (l/s) | Power (kW) | Efficiency (%) | Head (m) | Flow (l/s) | Efficiency (%)
Punjawa | 447 | 5 | Monoblock | 4.3814 | 20.9497 | 4.067 | 22.1402 | 5 | 26 | 46
Punjawa | 799 | 5 | Monoblock | 3.6382 | 26.0266 | 5.0795 | 18.2877 | 5 | 26 | 46
Punjawa | 3296 | 5 | Monoblock | 3.9342 | 17.1363 | 3.2126 | 20.5867 | 5 | 26 | 46
Punjawa | 2153 | 5 | Monoblock | 3.6888 | 19.0355 | 3.4277 | 20.0965 | 5 | 26 | 46
Punjawa | 1129 | 5 | Monoblock | 4.9873 | 21.4797 | 4.6617 | 22.5432 | 7 | 22.5 | 56
Punjawa | 426 | 5 | Monoblock | 4.3004 | 19.3757 | 4.9141 | 16.6337 | 5 | 26 | 46
Punjawa | 1114 | 5 | Monoblock | 5.0545 | 29.5955 | 5.1572 | 28.4549 | 5 | 26 | 46
Punjawa | 1172 | 5 | Monoblock | 5.3958 | 15.2827 | 3.8076 | 21.2455 | 6 | 19 | 39
Punjawa | 1123 | 5 | Monoblock | 3.7128 | 18.8206 | 6.0211 | 11.3849 | 5 | 26 | 46
Punjawa | 435 | 5 | Monoblock | 4.0068 | 19.698 | 4.531 | 17.088 | 5 | 26 | 46
Punjawa | 1115 | 5 | Monoblock | 4.7199 | 36.4964 | 4.3183 | 39.1323 | 5 | 26 | 46
Punjawa | 1140 | 5 | Monoblock | 4.828 | 24.9723 | 3.6547 | 32.3628 | 5 | 26 | 46
Punjawa | New Connection | 5 | Monoblock | 1.9345 | 33.7079 | 6.6084 | 9.68 | 5 | 26 | 46
Punjawa | 791 | 10 | Monoblock | 5.0746 | 38.5604 | 3.2366 | 59.3101 | 5 | 26 | 46
Punjawa | New Connection | 5 | Monoblock | 4.9937 | 28.2132 | 3.3407 | 41.372 | 5 | 26 | 46
Punjawa | 1092 | 5 | Monoblock | 4.3574 | 19.9137 | 5.3492 | 15.913 | 5 | 26 | 46
Punjawa | 3317 | 5 | Monoblock | 5.0966 | 24.1481 | 10.6557 | 11.3305 | 5 | 26 | 46
Punjawa | 1141 | 5 | Monoblock | 3.9311 | 24.9861 | 5.1173 | 18.8299 | 5 | 26 | 46
Punjawa | 1070 | 5 | Monoblock | 4.1118 | 23.1899 | 2.8554 | 32.759 | 5 | 26 | 46
Punjawa | 3297 | 5 | Monoblock | 4.9845 | 28.3554 | 3.3153 | 41.8218 | 5 | 26 | 46
Punjawa | 3309 | 5 | Monoblock | 4.7778 | 30.9598 | 6.0213 | 24.0995 | 5 | 26 | 46
Punjawa | 1173 | 5 | Monoblock | 3.6871 | 26.6667 | 4.4155 | 21.8446 | 5 | 26 | 46
Punjawa | 716 | 5 | Monoblock | 5.6887 | 18.9913 | 4.8483 | 21.8601 | 6 | 19 | 39
Punjawa | New Connection | 5 | Monoblock | 3.2503 | 22.927 | 5.0959 | 14.3454 | 5 | 26 | 46
Punjawa | 3321 | 5 | Monoblock | 3.6502 | 24.4366 | 4.85 | 18.0419 | 5 | 26 | 46
Punjawa | 1083 | 5 | Monoblock | 3.6507 | 22.2938 | 4.7408 | 16.8414 | 5 | 26 | 46
Punjawa | 1178 | 5 | Monoblock | 5.1947 | 18.711 | 4.7871 | 19.9182 | 5 | 26 | 46
Punjawa | 1096 | 5 | Monoblock | 4.2847 | 26.0191 | 5.7764 | 18.9334 | 5 | 26 | 46
Punjawa | 1094 | 5 | Monoblock | 4.2571 | 25.2525 | 6.3471 | 16.6155 | 5 | 26 | 46
Punjawa | 1095 | 5 | Monoblock | 3.2962 | 15.4639 | 4.4875 | 11.1429 | 5 | 26 | 46
Punjawa | 2147 | 5 | Monoblock | 4.0505 | 27.8638 | 5.535 | 20.0034 | 5 | 26 | 46
Punjawa | 1152 | 5 | Monoblock | 4.0155 | 19.5016 | 4.8714 | 15.77 | 5 | 26 | 46
Punjawa | New Connection |  | Monoblock | 4.4695 | 24.1158 | 6.0072 | 17.6017 | 5 | 26 | 46
Punjawa | New Connection | 5 | Monoblock | 3.7959 | 26.3543 | 4.3766 | 22.423 | 5 | 26 | 46
Punjawa | 3330 | 5 | Monoblock | 3.2738 | 14.7493 | 4.091 | 11.579 | 5 | 26 | 46
Punjawa | 519 | 5 | Monoblock | 4.5592 | 25.4741 | 5.0488 | 22.5666 | 5 | 26 | 46
Punjawa | 867 | 7.5 | Monoblock | 5.3983 | 34.9515 | 6.8493 | 27.0235 | 5 | 26 | 46
Punjawa | 696 |  | Monoblock | 4.3525 | 32.1543 | 4.0505 | 33.8955 | 5 | 26 | 46
Punjawa | 1122 | 5 | Monoblock | 4.558 | 24.9861 | 5.1173 | 21.8325 | 5 | 26 | 46
Punjawa | 465 | 5 | Monoblock | 4.7347 | 27.8638 | 4.8767 | 26.5388 | 5 | 26 | 46
Punjawa | New Connection | 15 | Monoblock | 4.2239 | 39.0964 | 5.1645 | 31.3683 | 5 | 26 | 46
Punjawa | New Connection | 5 | Monoblock | 3.9431 | 22.1839 | 5.6007 | 15.3215 | 5 | 26 | 46
Punjawa | New Connection | 5 | Monoblock | 4.4429 | 28.0987 | 9.1333 | 13.4089 | 5 | 26 | 46
Punjawa | New Connection | 5 | Monoblock | 4.1475 | 13.8058 | 2.9554 | 19.0065 | 5 | 26 | 46
Punjawa | New Connection | 5 | Monoblock | 4.0766 | 26.6115 | 4.8537 | 21.926 | 6 | 19 | 39
Punjawa | New Connection | 5 | Monoblock | 4.3864 | 22.2222 | 5.222 | 18.3116 | 5 | 26 | 46
Punjawa | New Connection | 5 | Monoblock | 4.9729 | 23.7404 | 5.843 | 19.8213 | 5 | 26 | 46
Punjawa | New Connection | 5 | Monoblock | 4.2031 | 28.0811 | 6.3397 | 18.2636 | 5 | 26 | 46
Punjawa | New Connection | 5 | Monoblock | 3.7595 | 25.9516 | 6.2747 | 15.2535 | 5 | 26 | 46
Punjawa | New Connection | 5 | Monoblock | 5.4154 | 22.5677 | 4.5246 | 26.4974 | 5 | 26 | 46
Punjawa | New Connection | 5 | Monoblock | 3.3752 | 18.4464 | 3.5485 | 17.2119 | 5 | 26 | 46
Punjawa | New Connection | 5 | Monoblock | 4.9262 | 19.5355 | 6.2033 | 15.2187 | 5 | 26 | 46
Punjawa | New Connection | 5 | Monoblock | 3.8829 | 23.5726 | 4.0742 | 22.0388 | 5 | 26 | 46
Punjawa | 1052 | 5 | Monoblock | 4.376 | 21.4388 | 4.12 | 22.3381 | 5 | 26 | 46
Punjawa | 1116 | 5 | Monoblock | 3.9753 | 17.3846 | 5.1523 | 13.1585 | 5 | 26 | 46
Punjawa | 1117 | 5 | Monoblock | 3.2965 | 16.4264 | 4.7104 | 11.2773 | 5 | 26 | 46
Punjawa | 1048 | 5 | Monoblock | 4.185 | 24.9931 | 5.6133 | 18.2797 | 5 | 26 | 46
Punjawa | 3290 | 5 | Monoblock | 4.0356 | 27.3556 | 4.9092 | 22.0605 | 5 | 26 | 46
Punjawa | 896 | 5 | Monoblock | 3.5726 | 23.7969 | 5.0811 | 16.414 | 5 | 26 | 46
Punjawa | 2155 | 5 | Monoblock | 3.5186 | 13.4529 | 3.1615 | 14.688 | 5 | 26 | 46
Punjawa | 1118 | 5 | Monoblock | 4.3227 | 19.1489 | 4.2617 | 19.054 | 5 | 26 | 46
Punjawa | New Connection | 5 | Monoblock | 5.3135 | 27.2975 | 5.3509 | 26.5916 | 5 | 26 | 46
Punjawa | 3340 | 5 | Monoblock | 5.0676 | 22.7848 | 3.7789 | 29.9742 | 5 | 26 | 46
Punjawa | 3318 | 5 | Monoblock | 4.319 | 26.7221 | 3.2793 | 34.5261 | 5 | 26 | 46
Punjawa | 3319 | 5 | Monoblock | 3.0046 | 17.4452 | 3.564 | 14.4276 | 5 | 26 | 46
Punjawa | 2149 | 5 | Monoblock | 4.1842 | 24.2001 | 3.4113 | 29.1193 | 5 | 26 | 46
Punjawa | New Connection | 5 | Monoblock | 3.6289 | 25.6191 | 4.022 | 22.676 | 5 | 26 | 46
Punjawa | 2293 | 5 | Monoblock | 3.7421 | 21.1268 | 6.1673 | 12.5754 | 5 | 26 | 46
Punjawa | 2326 | 5 | Monoblock | 4.608 | 26.5957 | 4.4175 | 27.2155 | 5 | 26 | 46
Punjawa | 2158 | 5 | Monoblock | 3.6718 | 18.6838 | 5.4479 | 12.3532 | 5 | 26 | 46
Punjawa | New Connection | 5 | Monoblock | 3.6993 | 19.4763 | 4.3056 | 16.4159 | 5 | 26 | 46
Punjawa | 1694 | 5 | Monoblock | 4.3002 | 26.738 | 5.3622 | 21.0353 | 5 | 26 | 46
Punjawa | 1691 | 5 | Monoblock | 4.8256 | 23.2108 | 4.0577 | 27.079 | 5 | 26 | 46
Punjawa | 1729 | 5 | Monoblock | 4.3966 | 21.9673 | 4.0291 | 23.5154 | 5 | 26 | 46
Punjawa | New Connection | 5 | Monoblock | 3.7713 | 26.6667 | 6.363 | 15.5049 | 5 | 26 | 46
Punjawa | 2329 | 5 | Monoblock | 4.0391 | 20.436 | 4.2475 | 19.0641 | 5 | 26 | 46
Punjawa | New connection |  | Monoblock | 3.4962 | 22.6757 | 4.9161 | 15.82 | 5 | 26 | 46
Punjawa | New connection |  | Monoblock | 5.2709 | 27.881 | 5.1763 | 27.8513 | 5 | 26 | 46
Punjawa | New connection |  | Monoblock | 3.6901 | 19.5101 | 4.1448 | 17.0396 | 5 | 26 | 46
Punjawa | New connection |  | Monoblock | 3.5886 | 16.5624 | 4.5326 | 12.8639 | 5 | 26 | 46
Punjawa | New connection | 5 | Monoblock | 2.3961 | 16.9555 | 3.479 | 11.456 | 5 | 26 | 46
Punjawa | sr. no.146 | 5 | Monoblock | 3.9572 | 18.5261 | 4.3003 | 16.724 | 5 | 26 | 46
Punjawa | 900 | 5 | Monoblock | 3.1615 | 17.1233 | 4.8185 | 11.0214 | 5 | 26 | 46
Punjawa | New Connection | 5 | Monoblock | 4.0058 | 21.3675 | 5.3509 | 15.6924 | 5 | 26 | 46
Punjawa | 2317 | 5 | Monoblock | 3.423 | 20.2657 | 4.5534 | 14.9455 | 5 | 26 | 46
Punjawa | 2356 | 5 | Monoblock | 4.0405 | 15.5226 | 3.9141 | 15.7191 | 5 | 26 | 46
Punjawa | New connection | 5 | Monoblock | 3.3257 | 17.4317 | 3.6615 | 15.5321 | 5 | 26 | 46
Punjawa | New Connection | 5 | Monoblock | 3.7527 | 20.7708 | 4.6103 | 16.586 | 5 | 26 | 46
Punjawa | 936 | 5 | Monoblock | 3.4353 | 20.7517 | 3.4931 | 20.0207 | 5 | 26 | 46
Punjawa | 935 | 5 | Monoblock | 3.573 | 24.1676 | 4.5418 | 18.6515 | 5 | 26 | 46
Punjawa | 2234 | 5 | Monoblock | 4.3353 | 8.7762 | 3.0665 | 12.1718 | 5 | 26 | 46
Punjawa | 2304 | 5 | Monoblock | 3.7966 | 12.3069 | 3.0846 | 14.8597 | 5 | 26 | 46
Punjawa | 1679 | 5 | Monoblock | 5.3735 | 14.3541 | 5.7719 | 13.1093 | 5 | 26 | 46
Punjawa | 1678 | 5 | Monoblock | 4.8525 | 27.4223 | 4.4329 | 29.4478 | 5 | 26 | 46
Punjawa | 1713 | 5 | Monoblock | 4.477 | 23.7404 | 3.339 | 31.2274 | 5 | 26 | 46
Punjawa | 718 | 5 | Monoblock | 5.4581 | 25.0417 | 4.0178 | 33.3727 | 5 | 26 | 46
Punjawa | 1688 | 5 | Monoblock | 4.5511 | 25.395 | 3.3372 | 33.974 | 5 | 26 | 46
Punjawa | 134 | 5 | Monoblock | 3.5694 | 24.855 | 4.852 | 17.9377 | 5 | 26 | 46
Punjawa | 1718 | 5 | Monoblock | 4.7526 | 14.2495 | 4.5446 | 14.6186 | 5 | 26 | 46
Punjawa | 1686 | 5 | Monoblock | 4.9194 | 27.1411 | 3.7565 | 34.8676 | 5 | 26 | 46
Punjawa | 164 | 5 | Monoblock | 4.6232 | 22.4439 | 4.2507 | 23.9468 | 5 | 26 | 46
Punjawa | 2236 | 5 | Monoblock | 5.6487 | 22.779 | 4.7821 | 26.3955 | 6 | 19 | 39
Punjawa | 1695 | 5 | Monoblock | 4.1365 | 14.1044 | 4.0391 | 14.17 | 5 | 26 | 46
Punjawa | 2233 | 5 | Monoblock | 3.931 | 17.1625 | 3.5 | 18.9098 | 5 | 26 | 46
Punjawa | 1640 | 5 | Monoblock | 4.2904 | 26.3312 | 4.7465 | 23.3487 | 5 | 26 | 46
Punjawa | 1641 | 5 | Monoblock | 4.2368 | 17.192 | 3.8157 | 18.7264 | 5 | 26 | 46
Punjawa | 148 | 10 | Monoblock | 3.9802 | 27.2645 | 4.7572 | 22.3777 | 5 | 26 | 46
Punjawa | New Connection | 5 | Monoblock | 3.8716 | 24.3969 | 7.2586 | 12.7656 | 5 | 26 | 46
Punjawa | 1639 | 5 | Monoblock | 4.2108 | 24.6171 | 4.3476 | 23.3894 | 5 | 26 | 46
Punjawa | 2309 | 5 | Monoblock | 4.7462 | 28.2663 | 5.8787 | 22.3875 | 5 | 26 | 46
Punjawa | 2378 | 5 | Monoblock | 3.7308 | 20.6564 | 6.1841 | 12.225 | 5 | 26 | 46
Punjawa | 2353 | 5 | Monoblock | 5.6924 | 13.6199 | 4.5211 | 16.8227 | 6 | 19 | 39
Punjawa | New Connection | 5 | Monoblock | 3.6177 | 17.8465 | 4.0839 | 15.5088 | 5 | 26 | 46
Punjawa | New Connection |  | Monoblock | 3.5872 | 31.8923 | 6.66 | 16.8515 | 5 | 26 | 46
Punjawa | New Connection |  | Monoblock | 2.9884 | 16.3785 | 3.5674 | 13.4592 | 5 | 26 | 46
Punjawa | 1631 |  | Monoblock | 1.7972 | 17.8465 | 5.3695 | 5.8598 | 5 | 26 | 46
Punjawa | New connection |  | Monoblock | 2.9192 | 29.8013 | 4.168 | 20.4755 | 5 | 26 | 46
Punjawa | 2325 |  | Monoblock | 2.7385 | 23.6469 | 4.5473 | 13.9702 | 5 | 26 | 46
Punjawa | New connection |  | Monoblock | 2.7091 | 24.57 | 5.3963 | 12.1004 | 5 | 26 | 46
Punjawa | 1732 |  | Monoblock | 2.822 | 20.979 | 4.6314 | 12.54 | 5 | 26 | 46
Punjawa | 1638 |  | Monoblock | 2.9848 | 24.6575 | 4.0739 | 17.7224 | 5 | 26 | 46
Punjawa | 166 |  | Monoblock | 2.6772 | 26.0116 | 5.648 | 12.0953 | 5 | 26 | 46
Punjawa | 141 |  | Monoblock | 2.0068 | 37.0218 | 5.0456 | 14.4447 | 5 | 26 | 46
Punjawa | 2055 |  | Monoblock | 7.978 | 23.8917 | 4.4216 | 42.2895 | 5 | 26 | 46
Punjawa | 2336 |  | Monoblock | 4.9662 | 23.3402 | 4.6956 | 24.2161 | 5 | 26 | 46
Punjawa | 1692 |  | Monoblock | 2.9955 | 30.2928 | 5.3028 | 16.7872 | 5 | 26 | 46
Punjawa | 1663 |  | Monoblock | 2.9958 | 16.7535 | 3.5896 | 13.7166 | 5 | 26 | 46
Punjawa | 2354 |  | Monoblock | 3.6386 | 25.2525 | 5.1537 | 17.49 | 5 | 26 | 46
Punjawa | 1746 |  | Monoblock | 3.1773 | 21.8076 | 4.9289 | 13.7905 | 5 | 26 | 46
Punjawa | 1757 |  | Monoblock | 2.8991 | 29.1923 | 4.577 | 18.1391 | 5 | 26 | 46
Punjawa | 1654 |  | Monoblock | 2.8322 | 20.9302 | 4.2477 | 13.6903 | 5 | 26 | 46
Punjawa | 890 |  | Monoblock | 2.6275 | 28.3465 | 5.4146 | 13.4942 | 5 | 26 | 46
Punjawa | 832 |  | Monoblock | 2.6549 | 15.3899 | 3.3199 | 12.0732 | 5 | 26 | 46
Punjawa | 2330 |  | Monoblock | 2.6164 | 28.5442 | 4.7855 | 15.3095 | 5 | 26 | 46
Punjawa | 1736 |  | Monoblock | 2.6187 | 23.7844 | 4.7829 | 12.7748 | 5 | 26 | 46
Punjawa | 2321 | 5 | Monoblock | 4.6555 | 20.7708 | 6.5246 | 14.5391 | 5 | 26 | 46
Punjawa | 2347 | 5 | Monoblock | 4.8279 | 24.4167 | 3.3468 | 34.5534 | 5 | 26 | 46
Punjawa | 2365 | 5 | Monoblock | 4.3424 | 21.2064 | 4.3276 | 20.8748 | 5 | 26 | 46
Punjawa | 1755 | 5 | Monoblock | 4.4394 | 29.7226 | 3.6164 | 35.7931 | 5 | 26 | 46
Punjawa | 2311 | 5 | Monoblock | 4.9005 | 18.1525 | 4.8537 | 17.9793 | 5 | 26 | 46
Punjawa | New Connection | 5 | Monoblock | 4.3531 | 19.9424 | 3.9753 | 21.4227 | 5 | 26 | 46
Punjawa | 529 | 5 | Monoblock | 4.1747 | 24.0449 | 5.2068 | 18.9122 | 5 | 26 | 46
Punjawa | 171 | 5 | Monoblock | 5.7663 | 25.3022 | 3.0855 | 46.3876 | 6 | 24.5 | 51
Punjawa | 905 | 5 | Monoblock | 3.858 | 23.7029 | 3.2354 | 27.7271 | 5 | 26 | 46
Punjawa | 2377 | 5 | Monoblock | 3.9462 | 17.9033 | 7.7023 | 8.9984 | 5 | 26 | 46
Punjawa | 2387 | 5 | Monoblock | 3.917 | 28.8 | 5.2494 | 21.0815 | 5 | 26 | 46
Punjawa | 2063 | 5 | Monoblock | 3.9264 | 21.6398 | 7.1281 | 11.6935 | 5 | 26 | 46
Punjawa | 844 | 5 | Monoblock | 4.1146 | 18.68 | 5.8623 | 12.862 | 5 | 26 | 46
Punjawa | 2301 | 5 | Monoblock | 3.6544 | 18.1671 | 4.3416 | 15.001 | 5 | 26 | 46
Punjawa | 2058 | 5 | Monoblock | 4.4465 | 22.5225 | 3.9891 | 24.6282 | 5 | 26 | 46
Punjawa | 1657 | 5 | Monoblock | 3.9657 | 21.9673 | 6.01 | 14.2196 | 5 | 26 | 46
Punjawa | 2372 | 5 | Monoblock | 3.4901 | 22.3436 | 3.8783 | 19.7249 | 5 | 26 | 46
Punjawa | 145 | 5 | Monoblock | 3.7343 | 21.0822 | 3.3867 | 22.8049 | 5 | 26 | 46
Punjawa | 1704 | 5 | Monoblock | 3.7136 | 20.5011 | 4.9863 | 14.9785 | 5 | 26 | 46
Punjawa | 144 | 5 | Monoblock | 4.0259 | 27.7949 | 4.7297 | 23.2096 | 5 | 26 | 46
Punjawa | new connection | 5 | Monoblock | 3.7866 | 22.4831 | 4.8935 | 17.0669 | 5 | 26 | 46
Punjawa | 135 | 7.5 | Monoblock | 4.8082 | 23.8095 | 3.7943 | 29.5981 | 5 | 26 | 46
Punjawa | New connection |  | Monoblock | 2.625 | 22.2277 | 4.7341 | 12.0908 | 5 | 26 | 46
Punjawa | New connection |  | Monoblock | 3.7368 | 27.2727 | 5.7624 | 17.3499 | 5 | 26 | 46
Punjawa | 2346 |  | Monoblock | 3.6063 | 16.1725 | 4.1779 | 13.6948 | 5 | 26 | 46
Punjawa | 153 |  | Monoblock | 3.6059 | 31.2283 | 4.3137 | 25.608 | 5 | 26 | 46
Punjawa | New connection |  | Monoblock | 3.2771 | 23.4926 | 3.944 | 19.149 | 5 | 26 | 46
Punjawa | 2335 | 5 | Monoblock | 7.191 | 19.8238 | 6.8129 | 20.5265 | 7 | 18.5 | 43
Punjawa | 898 | 5 | Monoblock | 4.0686 | 28.222 | 4.0859 | 27.5681 | 5 | 26 | 46
Punjawa | 2331 | 5 | Monoblock | 4.5903 | 30.2115 | 4.0023 | 33.9913 | 5 | 26 | 46
Punjawa | 2338 | 5 | Monoblock | 4.1753 | 24.1805 | 2.881 | 34.378 | 5 | 26 | 46
Punjawa | 130 | 10 | Monoblock | 8.5504 | 23.071 | 6.3223 | 30.6086 | 8 | 23 | 42
Punjawa | 151 | 5 | Monoblock | 5.9494 | 20.8478 | 4.0855 | 29.7819 | 6 | 24.5 | 51
Punjawa | 152 | 5 | Monoblock | 7.9503 | 28.6351 | 5.4062 | 41.3103 | 8 | 31 | 52
Punjawa | New Connection | 5 | Monoblock | 4.9892 | 21.3675 | 4.3411 | 24.091 | 5 | 26 | 46
Punjawa | 1761 | 5 | Monoblock | 3.6494 | 29.1734 | 4.5219 | 23.0971 | 5 | 26 | 46
Punjawa | New Connection | 5 | Monoblock | 4.4544 | 23.9425 | 3.6908 | 28.347 | 5 | 26 | 46
Punjawa | 2364 | 5 | Monoblock | 3.7722 | 21.7602 | 4.1907 | 19.2147 | 5 | 26 | 46
Punjawa | 1676 | 5 | Monoblock | 6.6923 | 28.3822 | 3.8232 | 48.7376 | 6 | 24.5 | 51
Punjawa | 1675 | 5 | Monoblock | 4.3978 | 21.3574 | 3.7785 | 24.3857 | 5 | 26 | 46
Punjawa | 1745 | 5 | Monoblock | 3.9633 | 22.3992 | 6.0554 | 14.382 | 5 | 26 | 46
Punjawa | 2065 | 5 | Monoblock | 3.9149 | 25.395 | 5.3677 | 18.1695 | 5 | 26 | 46
Punjawa | 1674 | 5 | Monoblock | 3.9147 | 25 | 3.7402 | 25.6692 | 5 | 26 | 46
Punjawa | 1766 | 5 | Monoblock | 3.7794 | 17.7235 | 3.6451 | 18.0278 | 5 | 26 | 46
Punjawa | 2064 | 5 | Monoblock | 4.5677 | 29.2588 | 5.0791 | 25.8125 | 5 | 26 | 46
Punjawa | 1720 | 5 | Monoblock | 3.7381 | 20.2384 | 4.4521 | 16.6701 | 5 | 26 | 46
Punjawa | New Connection | 5 | Monoblock | 4.1606 | 23.298 | 5.4221 | 17.5378 | 5 | 26 | 46
Punjawa | 2328 | 5 | Monoblock | 4.3698 | 34.4432 | 4.7838 | 30.8646 | 5 | 26 | 46
Punjawa | 615 | 5 | Monoblock | 3.8716 | 27.9764 | 6.3532 | 16.7246 | 5 | 26 | 46
Punjawa | 1648 | 5 | Monoblock | 4.0249 | 27.5566 | 4.4149 | 24.6449 | 5 | 26 | 46
Punjawa | 1719 |  | Monoblock | 3.8707 | 15.4932 | 5.3677 | 10.9599 | 5 | 26 | 46
Punjawa | New connection |  | Monoblock | 4.9411 | 19.1123 | 4.4487 | 20.8244 | 5 | 26 | 46
Punjawa | 1677 |  | Monoblock | 5.2953 | 10.459 | 5.3093 | 10.2333 | 6 | 19 | 39
Punjawa | 1557 |  | Monoblock | 3.829 | 13.9969 | 4.0323 | 13.0387 | 5 | 26 | 46
Punjawa | New connection |  | Monoblock | 3.4617 | 21.9566 | 5.2733 | 14.1398 | 5 | 26 | 46
Punjawa | 1633 |  | Monoblock | 5.0821 | 21.4797 | 4.6617 | 22.9716 | 5 | 26 | 46
Punjawa | 1762 |  | Monoblock | 4.7298 | 38.8601 | 3.9227 | 45.9649 | 5 | 26 | 46
Punjawa | 2231 |  | Monoblock | 4.5734 | 25.6337 | 3.7312 | 30.8228 | 5 | 26 | 46
Punjawa | 225 |  | Monoblock | 3.7669 | 21.7918 | 4.8854 | 16.4833 | 5 | 26 | 46
Punjawa | 963 |  | Monoblock | 5.423 | 24.2718 | 3.5084 | 36.8046 | 5 | 26 | 46
Punjawa | 559 |  | Monoblock | 3.8998 | 16.9205 | 4.8223 | 13.4237 | 5 | 26 | 46
Punjawa | 155 | 5 | Monoblock | 5.1501 | 25.1607 | 3.6577 | 34.7539 | 5 | 26 | 46
Punjawa | 2067 | 5 | Monoblock | 4.6476 | 26.6115 | 4.8537 | 24.9969 | 5 | 26 | 46
Punjawa | 1733 | 5 | Monoblock | 4.5938 | 26.7062 | 4.2812 | 28.1117 | 5 | 26 | 46
Punjawa | New Connection | 5 | Monoblock | 4.6993 | 22.2552 | 3.5909 | 28.5712 | 5 | 26 | 46
Punjawa | New Connection | 5 | Monoblock | 4.1853 | 24.2261 | 3.4664 | 28.6946 | 5 | 26 | 46
Punjawa | 796 | 5 | Monoblock | 4.3492 | 20.7326 | 2.9928 | 29.5563 | 5 | 26 | 46
Punjawa | 2375 | 5 | Monoblock | 4.2375 | 38.8601 | 3.9227 | 41.1802 | 5 | 26 | 46
Punjawa | 1742 | 5 | Monoblock | 3.3977 | 29.654 | 6.1774 | 16.0005 | 5 | 26 | 46
Punjawa | New connection | 5 | Monoblock | 6.7287 | 24.0706 | 5.8551 | 27.1366 | 7 | 22.5 | 56
Punjawa | 139 | 5 | Monoblock | 3.6062 | 14.6819 | 3.3629 | 15.4449 | 5 | 26 | 46
Punjawa | 2296 | 5 | Monoblock | 3.7361 | 20.9644 | 3.8087 | 20.1739 | 5 | 26 | 46
Punjawa | 2352 | 5 | Monoblock | 3.7893 | 18.1123 | 4.3841 | 15.3576 | 5 | 26 | 46
Punjawa | 2295 | 5 | Monoblock | 4.0654 | 28.5987 | 3.8447 | 29.6653 | 5 | 26 | 46
Punjawa | 1650 | 5 | Monoblock | 3.4546 | 10.9436 | 3.6711 | 10.1026 | 5 | 26 | 46
Punjawa | 1649 | 5 | Monoblock | 3.5538 | 15.5387 | 4.5005 | 12.037 | 5 | 26 | 46
Punjawa | 2297 | 5 | Monoblock | 3.5648 | 15.8284 | 3.4613 | 15.9921 | 5 | 26 | 46
Punjawa | New Connection | 5 | Monoblock | 4.4077 | 22.596 | 5.7896 | 16.8759 | 5 | 26 | 46
Punjawa | 1721 | 5 | Monoblock | 4.0255 | 20.6992 | 6.0668 | 13.4736 | 5 | 26 | 46
Punjawa | 1731 | 5 | Monoblock | 3.7851 | 17.9069 | 3.8254 | 17.3818 | 5 | 26 | 46
Punjawa | 1662 | 5 | Monoblock | 4.1023 | 28.0374 | 5.4403 | 20.7403 | 5 | 26 | 46
Punjawa | new connection | 5 | Monoblock | 4.8221 | 30.6958 | 6.6569 | 21.8125 | 5 | 26 | 46
Punjawa | 2062 | 5 | Monoblock | 5.9757 | 32.5733 | 4.613 | 41.3937 | 5 | 26 | 46
Punjawa | 916 | 5 | Monoblock | 4.848 | 24.3243 | 6.0433 | 19.1425 | 5 | 26 | 46
Punjawa | 535 | 5 | Monoblock | 4.8766 | 18.8206 | 4.102 | 21.9492 | 5 | 26 | 46
Punjawa | 2394 | 5 | Monoblock | 4.1286 | 30.0802 | 7.1188 | 17.114 | 5 | 26 | 46
Punjawa | 1715 | 5 | Monoblock | 3.4342 | 20.4128 | 5.0227 | 13.6918 | 5 | 26 | 46
Punjawa | 1886 | 5 | Monoblock | 2.8268 | 20.3252 | 3.8139 | 14.7786 | 5 | 26 | 46
Punjawa | 1699 | 5 | Monoblock | 2.9811 | 23.3584 | 4.323 | 15.8015 | 5 | 26 | 46
Punjawa | 1697 | 5 | Monoblock | 3.1794 | 21.6972 | 4.4816 | 15.1 | 5 | 26 | 46
Punjawa | 952 | 5 | Monoblock | 2.3358 | 21.7024 | 4.1255 | 12.0544 | 5 | 26 | 46
Punjawa | 939 | 5 | Monoblock | 3.4119 | 23.3402 | 4.2829 | 18.2404 | 5 | 26 | 46
Punjawa | 1698 | 5 | Monoblock | 3.1051 | 26.8336 | 4.7285 | 17.286 | 5 | 26 | 46
Punjawa | 1669 | 5 | Monoblock | 4.3734 | 19.5228 | 4.1523 | 20.1716 | 5 | 26 | 46
Punjawa | new connection | 5 | Monoblock | 3.7229 | 27.4056 | 4.6481 | 21.5337 | 5 | 26 | 46
Punjawa | 138 | 5 | Monoblock | 3.1371 | 26.8817 | 5.0046 | 16.5307 | 5 | 26 | 46
Punjawa | New Connection | 5 | Monoblock | 5.3917 | 18.5644 | 4.0192 | 24.4307 | 5 | 26 | 46
Punjawa | 1170 | 5 | Monoblock | 7.821 | 17.9069 | 3.8972 | 35.2528 | 8 | 17.8 | 47
Punjawa | 877 | 5 | Monoblock | 6.8892 | 26.4628 | 5.1944 | 34.4297 | 7 | 22.5 | 56
Punjawa | 1645 | 5 | Monoblock | 4.5549 | 16.9843 | 3.9099 | 19.4102 | 5 | 26 | 46
Punjawa | 170 | 5 | Monoblock | 5.0104 | 11.7894 | 4.5526 | 12.7284 | 5 | 26 | 46
Punjawa | 154 | 5 | Monoblock | 3.4583 | 15.2181 | 3.9166 | 13.1817 | 5 | 26 | 46
Punjawa | sr. no.148 | 5 | Monoblock | 4.2714 | 22.3936 | 4.2292 | 22.1875 | 5 | 26 | 46
Punjawa | 1644 | 5 | Monoblock | 3.8718 | 15.6549 | 4.9716 | 11.9602 | 5 | 26 | 46
Punjawa | 1730 | 5 | Monoblock | 4.2102 | 16.5807 | 4.9869 | 13.7324 | 5 | 26 | 46
Punjawa | 1724 | 5 | Monoblock | 4.2636 | 18.572 | 4.23 | 18.3637 | 5 | 26 | 46
Punjawa | 2310 | 5 | Monoblock | 4.019 | 20.0401 | 4.6488 | 16.9961 | 5 | 26 | 46
Punjawa | 1749 | 5 | Monoblock | 4.8695 | 17.3913 | 6.9146 | 12.0149 | 5 | 26 | 46
Punjawa | 1754 | 5 | Monoblock | 3.9446 | 16.4114 | 4.6168 | 13.7553 | 5 | 26 | 46
Punjawa | 2363 | 5 | Monoblock | 3.9738 | 16.2162 | 3.348 | 18.8817 | 5 | 26 | 46
Punjawa | 2397 | 5 | Monoblock | 5.417 | 22.5282 | 5.898 | 20.2977 | 5 | 26 | 46
Punjawa | 168 | 5 | Monoblock | 5.2812 | 20.8768 | 9.2036 | 11.7519 | 5 | 26 | 46
Punjawa | New Connection | 5 | Monoblock | 4.9521 | 21.3777 | 3.3958 | 30.5826 | 5 | 26 | 46
Punjawa | New Connection | 5 | Monoblock | 4.6178 | 27.4223 | 4.7773 | 26.0031 | 5 | 26 | 46
Punjawa | 1665 | 5 | Monoblock | 4.3564 | 20.766 | 3.2406 | 27.3861 | 5 | 26 | 46
Punjawa | 2298 | 5 | Monoblock | 4.9209 | 31.2609 | 5.22 | 28.9099 | 5 | 26 | 46
Punjawa | 1727 | 5 | Monoblock | 4.475 | 24.2457 | 3.6012 | 29.5564 | 5 | 26 | 46
Punjawa | 1744 | 5 | Monoblock | 4.7545 | 22.2772 | 5.889 | 17.644 | 5 | 26 | 46
Punjawa | 2360 | 5 | Monoblock | 9.9436 | 24.6846 | 5.8975 | 40.8289 | 11.9 | 25 | 52
Punjawa | 1703 | 5 | Monoblock | 7.1255 | 19.3507 | 4.097 | 33.0154 | 7 | 22.5 | 56
Punjawa | 1702 | 5 | Monoblock | 3.7415 | 14.6246 | 4.1574 | 12.9116 | 5 | 26 | 46
Punjawa | 2370 | 5 | Monoblock | 4.7595 | 23.012 | 4.9719 | 21.6107 | 5 | 26 | 46
Punjawa | 1725 | 5 | Monoblock | 3.7762 | 10.7347 | 6.762 | 5.8808 | 5 | 26 | 46
Punjawa | 806 | 5 | Monoblock | 4.1598 | 22.2332 | 4.6182 | 19.6459 | 5 | 26 | 46
Punjawa | 999 | 5 | Monoblock | 5.1439 | 24.2196 | 5.4305 | 22.5054 | 5 | 26 | 46
Punjawa | 2322 | 5 | Monoblock | 4.1596 | 15.015 | 3.9667 | 15.4459 | 5 | 26 | 46
Punjawa | 137 | 5 | Monoblock | 4.015 | 20.2384 | 3.8672 | 20.6126 | 5 | 26 | 46
Punjawa | 2323 | 5 | Monoblock | 4.1539 | 23.86 | 4.8067 | 20.2282 | 5 | 26 | 46
Punjawa | 167 | 5 | Monoblock | 4.0354 | 19.6121 | 5.1539 | 15.0642 | 5 | 26 | 46
Punjawa | 1637 | 5 | Monoblock | 3.3294 | 25.7363 | 5.476 | 15.3502 | 5 | 26 | 46
Punjawa | 163 | 5 | Monoblock | 4.4919 | 23.7279 | 3.9687 | 26.346 | 5 | 26 | 46
Punjawa | sr. no.130 | 5 | Monoblock | 4.3948 | 22.6244 | 5.8079 | 16.7946 | 5 | 26 | 46
Punjawa | 1759 | 5 | Monoblock | 4.6356 | 19.3632 | 4.9188 | 17.9016 | 5 | 26 | 46
Punjawa | 2316 | 5 | Monoblock | 4.6353 | 24.3375 | 6.4198 | 17.2387 | 5 | 26 | 46
Punjawa | new connection | 5 | Monoblock | 4.7337 | 23.31 | 5.8447 | 18.5204 | 5 | 26 | 46
Punjawa | 513 | 5 | Monoblock | 5.2131 | 26.1097 | 6.5395 | 20.4183 | 5 | 26 | 46
Punjawa | New Connection | 5 | Monoblock | 4.1304 | 23.5664 | 4.8415 | 19.7232 | 5 | 26 | 46
Punjawa | 2294 | 5 | Monoblock | 4.2204 | 22.1293 | 5.2206 | 17.5495 | 5 | 26 | 46
Punjawa | 2300 | 5 | Monoblock | 5.3484 | 22.5507 | 4.9139 | 24.0786 | 5 | 26 | 46
Punjawa | New Connection | 5 | Monoblock | 4.9741 | 21.2988 | 5.8617 | 17.7302 | 5 | 26 | 46
Punjawa | 887 |  | Monoblock | 4.4819 | 21.8797 | 4.1525 | 23.1667 | 5 | 26 | 46
Punjawa | sr. no.156 |  | Monoblock | 6.8183 | 25.7216 | 5.7659 | 29.8383 | 7 | 22.5 | 56
Punjawa | 918 |  | Monoblock | 7.4206 | 26.6115 | 4.1777 | 46.3702 | 7 | 22.5 | 56
Punjawa | 2359 |  | Monoblock | 6.8344 | 11.3881 | 4.0129 | 19.0266 | 7 | 22.5 | 56
Punjawa | 2324 |  | Monoblock | 6.9451 | 23.5664 | 4.7994 | 33.455 | 7 | 22.5 | 56
Punjawa | 2319 |  | Monoblock | 4.5044 | 24.4233 | 4.2782 | 25.2262 | 5 | 26 | 46
Punjawa | 2308 |  | Monoblock | 6.559 | 21.8553 | 4.6523 | 30.227 | 7 | 22.5 | 56
Punjawa | New Connection | 5 | Monoblock | 4.1467 | 23.8727 | 3.3301 | 29.1618 | 5 | 26 | 46
Punjawa | 1666 | 5 | Monoblock | 4.5351 | 25.4309 | 5.3929 | 20.9793 | 5 | 26 | 46
Punjawa | 1022 | 5 | Monoblock | 4.6375 | 27.6158 | 5.4813 | 22.9209 | 5 | 26 | 46
Punjawa | 140 | 5 | Monoblock | 4.7955 | 31.679 | 3.6295 | 41.0602 | 5 | 26 | 46
Punjawa | 1643 | 5 | Monoblock | 4.4278 | 22.5734 | 3.2391 | 30.2712 | 5 | 26 | 46
Punjawa | 146 | 5 | Monoblock | 4.6169 | 30.3337 | 5.7168 | 24.0323 | 5 | 26 | 46
Punjawa | 683 | 5 | Monoblock | 4.3762 | 29.4214 | 4.7163 | 26.7811 | 5 | 26 | 46
Punjawa | 1716 | 5 | Monoblock | 4.1327 | 22.6415 | 4.3052 | 21.3216 | 5 | 26 | 46
Punjawa | 160 | 5 | Monoblock | 4.1301 | 22.579 | 4.436 | 20.6226 | 5 | 26 | 46
Punjawa | New Connection | 5 | Monoblock | 6.6064 | 22.2938 | 4.7427 | 30.4643 | 7 | 22.5 | 56
Punjawa | 1093 | 5 | Monoblock | 4.6479 | 19.8238 | 4.3869 | 20.6041 | 5 | 26 | 46
Punjawa | New Connection | 5 | Monoblock | 3.8487 | 33.0882 | 4.0962 | 30.4984 | 5 | 26 | 46
Punjawa | 1642 | 5 | Monoblock | 4.9727 | 19.9159 | 3.967 | 24.4901 | 5 | 26 | 46
Punjawa | 928 | 5 | Monoblock | 7.4605 | 27.3473 | 4.0606 | 49.2901 | 7 | 22.5 | 56
Punjawa | 1680 | 5 | Monoblock | 3.6229 | 28.7816 | 5.2038 | 19.6573 | 5 | 26 | 46
Punjawa | 1706 | 5 | Monoblock | 4.3214 | 20.7804 | 3.7596 | 23.432 | 5 | 26 | 46
Punjawa | 161 |  | Monoblock | 3.8092 | 12.6707 | 3.2321 | 14.6497 | 5 | 26 | 46
Punjawa | 2337 | 5 | Monoblock | 4.1637 | 19.8238 | 5.23 | 15.4823 | 5 | 26 | 46
Punjawa | 1671 | 5 | Monoblock | 4.1839 | 16.0456 | 3.4334 | 19.1814 | 5 | 26 | 46
Punjawa | New connection | 5 | Monoblock | 4.7002 | 21.6086 | 3.6932 | 26.9779 | 5 | 26 | 46
Punjawa | 2312 | 5 | Monoblock | 12.0221 | 25.9291 | 5.8707 | 52.0894 | 12 | 24 | 62
Punjawa | sr. no.131 | 5 | Monoblock | 8.1208 | 13.1791 | 5.387 | 19.4896 | 8 | 13.5 | 36
Punjawa | New connection | 5 | Monoblock | 8.1759 | 22.0049 | 5.0464 | 34.9736 | 8 | 20 | 59
Punjawa | 1664 | 5 | Monoblock | 4.3984 | 25.9815 | 4.1904 | 26.753 | 5 | 26 | 46
Punjawa | 1693 | 5 | Monoblock | 4.7214 | 23.0003 | 3.8753 | 27.4898 | 5 | 26 | 46
Punjawa | 1090 | 5 | Monoblock | 4.9697 | 21.1815 | 4.4059 | 23.4381 | 5 | 26 | 46
Punjawa | 1758 | 5 | Monoblock | 4.4368 | 22.965 | 5.0429 | 19.821 | 5 | 26 | 46
Punjawa | 819 | 5 | Monoblock | 4.9366 | 23.9744 | 5.299 | 21.9104 | 5 | 26 | 46
Punjawa | 1651 | 5 | Monoblock | 5.5718 | 28.6898 | 6.2831 | 24.9584 | 5 | 26 | 46
Punjawa | New connection | 5 | Monoblock | 4.2391 | 26.2467 | 5.259 | 20.7549 | 5 | 26 | 46
Punjawa | 2357 | 5 | Monoblock | 4.4107 | 22.4944 | 7.3479 | 13.246 | 5 | 26 | 46
Punjawa | 2060 | 5 | Monoblock | 4.7115 | 22.5677 | 4.1699 | 25.0146 | 5 | 26 | 46
Punjawa | 2361 | 5 | Monoblock | 4.5256 | 21.449 | 3.8526 | 24.7171 | 5 | 26 | 46
Punjawa | 2313 | 5 | Monoblock | 4.3284 | 23.071 | 4.6048 | 21.2743 | 5 | 26 | 46
Punjawa | New Connection | 5 | Monoblock | 4.6201 | 19.5016 | 3.141 | 28.1397 | 5 | 26 | 46
Punjawa | New Connection | 5 | Monoblock | 4.6194 | 19.9291 | 3.0205 | 29.8992 | 5 | 26 | 46
Punjawa | 548 | 5 | Monoblock | 4.4292 | 22.779 | 4.7821 | 20.6969 | 5 | 26 | 46
Punjawa | 2054 | 5 | Monoblock | 4.1169 | 22.7733 | 3.1818 | 28.907 | 5 | 26 | 46
Punjawa | 1714 | 5 | Monoblock | 4.8023 | 24.7729 | 3.9232 | 29.7477 | 5 | 26 | 46
Punjawa | New Connection | 5 | Monoblock | 6.9623 | 16.2455 | 4.7924 | 23.1525 | 7 | 18.5 | 43
Punjawa | 2302 | 5 | Monoblock | 3.3959 | 19.2308 | 4.3946 | 14.5783 | 5 | 26 | 46
Punjawa | sr.no.168 | 5 | Monoblock | 3.3772 | 23.5973 | 4.0983 | 19.0759 | 5 | 26 | 46
Punjawa | 1656 | 5 | Monoblock | 4.8866 | 18.6877 | 6.8451 | 13.0874 | 5 | 26 | 46
Punjawa | 872 | 5 | Monoblock | 3.0288 | 25.6337 | 5.5588 | 13.7015 | 5 | 26 | 46
Punjawa | 1647 | 5 | Monoblock | 4.8373 | 27.8035 | 4.1964 | 31.4407 | 5 | 26 | 46
Punjawa | 577 | 5 | Monoblock | 3.6124 | 24.8687 | 6.2457 | 14.1103 | 5 | 26 | 46
Punjawa | sr.no.157 | 5 | Monoblock | 3.9561 | 32.0399 | 7.0682 | 17.5923 | 5 | 26 | 46
Punjawa | 2379 | 5 | Monoblock | 3.9114 | 24.2001 | 3.9398 | 23.5692 | 5 | 26 | 46
Punjawa | new connection | 5 | Monoblock | 8.6557 | 19.1367 | 5.244 | 30.9867 | 9 | 17 | 50
Punjawa | New Connection | 5 | Monoblock | 8.3858 | 20.3989 | 4.0882 | 41.0473 | 9 | 17 | 50
Punjawa | New Connection | 5 | Monoblock | 5.6782 | 21.322 | 4.0227 | 29.5249 | 6 | 24.5 | 51
Punjawa | 2227 | 5 | Monoblock | 3.628 | 17.616 | 4.3081 | 14.5528 | 5 | 26 | 46
Punjawa | 817 | 10 | Monoblock | 3.7872 | 26.938 | 5.1562 | 19.4099 | 5 | 26 | 46
Punjawa | 2228 |  | Monoblock | 3.8851 | 23.622 | 4.5713 | 19.6947 | 5 | 26 | 46
Punjawa | 2343 | 5 | Monoblock | 4.3709 | 20.6849 | 3.0314 | 29.2583 | 5 | 26 | 46
Punjawa | New Connection | 5 | Monoblock | 3.6742 | 19.6635 | 3.5352 | 20.0487 | 5 | 26 | 46
Punjawa | 124 | 5 | Monoblock | 4.3082 | 27.3224 | 4.6852 | 24.6461 | 5 | 26 | 46
Punjawa | New Connection | 5 | Monoblock | 3.9755 | 19.4721 | 4.6849 | 16.2098 | 5 | 26 | 46
Punjawa | 1709 | 5 | Monoblock | 3.6383 | 18.2297 | 4.7908 | 13.5813 | 5 | 26 | 46
Punjawa | Sr. no. 135 | 5 | Monoblock | 4.1482 | 23.9107 | 4.6635 | 20.8645 | 5 | 26 | 46
Punjawa | 1646 | 5 | Monoblock | 5.3928 | 10.989 | 3.6982 | 15.72 | 5 | 26 | 46
Punjawa | 2241 | 5 | Monoblock | 4.8485 | 17.5131 | 3.3961 | 24.5274 | 5 | 26 | 46
Punjawa | New Connection | 5 | Monoblock | 5.9188 | 18.5414 | 4.9369 | 21.8066 | 6 | 24.5 | 51
Punjawa | 2305 | 5 | Monoblock | 4.9962 | 27.2562 | 3.5272 | 37.8737 | 5 | 26 | 46
Punjawa | 2235 |  | Monoblock | 4.4594 | 28.5896 | 6.012 | 20.8034 | 5 | 26 | 46
Punjawa | 1652 | 5 | Monoblock | 3.5845 | 22.4607 | 5.1199 | 15.4262 | 5 | 26 | 46
Punjawa | 2384 | 5 | Monoblock | 3.8251 | 13.8334 | 3.1044 | 16.721 | 5 | 26 | 46
Punjawa | 2398 | 5 | Monoblock | 4.0463 | 21.2766 | 5.2303 | 16.1474 | 5 | 26 | 46
Punjawa | 891 | 5 | Monoblock | 3.7991 | 12.8096 | 3.2414 | 14.7283 | 5 | 26 | 46
Punjawa | 2409 | 5 | Monoblock | 4.8724 | 55.6586 | 4.714 | 56.4347 | 5 | 26 | 46
Punjawa | 2348 | 5 | Monoblock | 5.5734 | 19.6893 | 6.345 | 16.9663 | 6 | 24.5 | 51
Punjawa | 2403 | 5 | Monoblock | 5.1739 | 24.4233 | 3.3873 | 36.5962 | 5 | 26 | 46
Punjawa | New Connection | 5 | Monoblock | 4.5292 | 16.4354 | 4.0467 | 18.0455 | 5 | 26 | 46

## Muthianwala
Feeder Name | Account No. | Connected HP / Sanctioned Demand | Type of Pump | Existing Pump Set Measured Parameters |  |  |  | Energy Efficient Pump Sets Parameters
|  |  |  | Total Head (m) | Flow (l/s) | Power (kW) | Efficiency (%) | Head (m) | Flow (l/s) | Efficiency (%)
Muthianwala | New Connection |  | Submersible | 14.7342 | 33.2349 | 11.3833 | 42.2009 | 14.7342 | 33.2349 | 64
Muthianwala | JM - 1042 |  | Submersible | 14.3744 | 27.1821 | 11.9614 | 32.045 | 14.3744 | 27.1821 | 62.4
Muthianwala | New Connection |  | Submersible | 14.7815 | 32.6323 | 7.9376 | 59.6136 | 14.7815 | 32.6323 | 64
Muthianwala | JB - 133 |  | Submersible | 15.2287 | 37.2517 | 12.8358 | 43.3567 | 15.2287 | 37.2517 | 64
Muthianwala | New Connection | 7.5 | Submersible | 12.9697 | 17.081 | 5.102 | 42.596 | 12.9697 | 17.081 | 60
Muthianwala | New Connection | 10 | Submersible | 13.8403 | 28.8554 | 8.2945 | 47.2335 | 13.8403 | 28.8554 | 64
Muthianwala | New Connection | 10 | Submersible | 13.6447 | 26.6667 | 6.5564 | 54.4423 | 13.6447 | 26.6667 | 62.4
Muthianwala | New Connection | 7.5 | Submersible | 8.9572 | 24.6778 | 10.2027 | 21.2535 | 8.9572 | 24.6778 | 62.4
Muthianwala | New Connection | 7.5 | Submersible | 13.5109 | 24.4432 | 10.0464 | 32.2478 | 13.5109 | 24.4432 | 62.4
Muthianwala | New Connection | 7.5 | Submersible | 13.6462 | 25.2242 | 10.8581 | 31.0989 | 13.6462 | 25.2242 | 62.4
Muthianwala | JM - 710 | 7.5 | Submersible | 13.4912 | 18.9514 | 8.2907 | 30.2531 | 13.4912 | 18.9514 | 58.5
Muthianwala | JM - 916 | 7.5 | Submersible | 15.4285 | 12.8333 | 7.4368 | 26.1185 | 15.4285 | 12.8333 | 57.75
Muthianwala | New Connection | 7.5 | Submersible | 13.8044 | 23.6904 | 7.9984 | 40.1104 | 13.8044 | 23.6904 | 62.4
Muthianwala | New Connection | 7.5 | Submersible | 14.8694 | 28.5805 | 12.2127 | 34.1365 | 14.8694 | 28.5805 | 64
Muthianwala | New Connection | 7.5 | Submersible | 13.8019 | 24.6778 | 10.2027 | 32.749 | 13.8019 | 24.6778 | 62.4
Muthianwala | New Connection | 7.5 | Submersible | 13.8178 | 14.6318 | 8.1877 | 24.2238 | 13.8178 | 14.6318 | 60
Muthianwala | New Connection | 7.5 | Submersible | 13.7381 | 24.2849 | 6.9209 | 47.2899 | 13.7381 | 24.2849 | 62.4
Muthianwala | New Connection | 7.5 | Submersible | 13.5674 | 21.4031 | 6.8006 | 41.8886 | 13.5674 | 21.4031 | 59.28
Muthianwala | New Connection | 7.5 | Submersible | 13.1885 | 20.4221 | 9.0662 | 29.1432 | 13.1885 | 20.4221 | 59.28
Muthianwala | New Connection | 7.5 | Submersible | 13.9551 | 20.7373 | 6.3524 | 44.6908 | 13.9551 | 20.7373 | 59.28
Muthianwala | JT - 456 | 7.5 | Submersible | 17.2753 | 28.4181 | 9.3961 | 51.2557 | 17.2753 | 28.4181 | 64
Muthianwala | JM - 129 | 7.5 | Submersible | 13.6462 | 13.8419 | 6.9598 | 26.6244 | 13.6462 | 13.8419 | 58.5
Muthianwala | JM - 926 | 7.5 | Submersible | 15.2828 | 13.8206 | 6.5589 | 31.5913 | 15.2828 | 13.8206 | 58.5
Muthianwala | JB - 931 | 7.5 | Submersible | 18.7026 | 25.4741 | 11.2139 | 41.6786 | 18.7026 | 25.4741 | 60.06
Muthianwala | JM - 1097 |  | Submersible | 17.5745 | 28.1426 | 8.9767 | 54.0502 | 17.5745 | 28.1426 | 64
Muthianwala | JM - 76 |  | Submersible | 17.3619 | 28.7173 | 9.3359 | 52.3907 | 17.3619 | 28.7173 | 64
Muthianwala | JB - 809 |  | Submersible | 17.7825 | 16.1406 | 7.3436 | 38.3418 | 17.7825 | 16.1406 | 60
Muthianwala | New Connection |  | Submersible | 19.8308 | 24.5165 | 10.3302 | 46.1698 | 19.8308 | 24.5165 | 60.8
Muthianwala | New Connection |  | Submersible | 17.8597 | 30.3849 | 9.8347 | 54.1303 | 17.8597 | 30.3849 | 56.16
Muthianwala | JM - 239 |  | Submersible | 16.9993 | 17.9176 | 7.8292 | 38.1649 | 16.9993 | 17.9176 | 59.28
Muthianwala | JB - 350 | 7.5 | Submersible | 14.1014 | 26.8898 | 7.9631 | 46.7129 | 14.1014 | 26.8898 | 62.4
Muthianwala | JB - 477 | 7.5 | Submersible | 14.5173 | 28.4991 | 8.965 | 45.2723 | 14.5173 | 28.4991 | 64
Muthianwala | JB - 396 |  | Submersible | 14.9386 | 36.4078 | 9.5931 | 55.618 | 14.9386 | 36.4078 | 64
Muthianwala | JB - 972 | 10 | Submersible | 13.8835 | 16.5807 | 6.6997 | 33.7065 | 13.8835 | 16.5807 | 60
Muthianwala | JB - 1103 | 7.5 | Submersible | 13.3261 | 20.5011 | 5.3479 | 50.1148 | 13.3261 | 20.5011 | 59.28
Muthianwala | New Connection | 7.5 | Submersible | 13.0124 | 14.985 | 4.9109 | 38.951 | 13.0124 | 14.985 | 57.75
Muthianwala | JB - 264 | 7.5 | Submersible | 14.5166 | 32.2004 | 9.0036 | 50.9302 | 14.5166 | 32.2004 | 64
Muthianwala | JB - 421 | 7.5 | Submersible | 13.9032 | 22.1076 | 9.9043 | 30.4439 | 13.9032 | 22.1076 | 58.52
Muthianwala | JB - 818 | 7.5 | Submersible | 14.1941 | 21.6398 | 13.0215 | 23.1404 | 14.1941 | 21.6398 | 58.52
Muthianwala | New Connection | 7.5 | Submersible | 14.6648 | 29.6638 | 8.5093 | 50.1511 | 14.6648 | 29.6638 | 64
Muthianwala | JB - 981 | 7.5 | Submersible | 13.9651 | 22.9533 | 8.1335 | 38.6618 | 13.9651 | 22.9533 | 62.4
Muthianwala | JB - 575 | 7.5 | Submersible | 13.6589 | 23.9107 | 7.4078 | 43.2501 | 13.6589 | 23.9107 | 62.4
Muthianwala | JB - 1136 | 7.5 | Submersible | 13.8747 | 25.6703 | 7.4651 | 46.8041 | 13.8747 | 25.6703 | 62.4
Muthianwala | JB - 940 | 7.5 | Submersible | 13.5711 | 25.7954 | 5.8986 | 58.2202 | 13.5711 | 25.7954 | 62.4
Muthianwala | JB - 1020 | 7.5 | Submersible | 14.3772 | 23.9489 | 7.7796 | 43.418 | 14.3772 | 23.9489 | 62.4
Muthianwala | R2 - 318 | 7.5 | Submersible | 12.6738 | 20.6992 | 8.4883 | 30.3188 | 12.6738 | 20.6992 | 59.28
Muthianwala | R2 - 311 | 7.5 | Submersible | 11.1532 | 34.2335 | 9.0573 | 41.3543 | 11.1532 | 34.2335 | 60
Muthianwala | R2 - 294 | 7.5 | Monoblock | 9.4383 | 23.9553 | 5.1573 | 43.0071 | 9.4383 | 23.9553 | 59.28
Muthianwala | New Connection | 7.5 | Submersible | 13.3524 | 20.8526 | 5.7675 | 47.3592 | 13.3524 | 20.8526 | 59.28
Muthianwala | JM - 957 | 7.5 | Submersible | 18.597 | 19.0315 | 7.658 | 45.3389 | 18.597 | 19.0315 | 59.28
Muthianwala | JB - 178 | 7.5 | Submersible | 16.0994 | 17.6852 | 4.8378 | 57.7355 | 16.0994 | 17.6852 | 59.28
Muthianwala | JB - 168 | 7.5 | Submersible | 17.7555 | 35.4052 | 10.5246 | 58.5955 | 17.7555 | 35.4052 | 60
Muthianwala | JB - 1113 | 7.5 | Submersible | 13.5956 | 19.6635 | 6.957 | 37.6972 | 13.5956 | 19.6635 | 59.28
Muthianwala | JB - 249 | 7.5 | Submersible | 14.1303 | 15.7178 | 8.1197 | 26.8332 | 14.1303 | 15.7178 | 60
Muthianwala | R2 - 108 | 7.5 | Submersible | 13.5947 | 24.1935 | 8.3037 | 38.8564 | 13.5947 | 24.1935 | 62.4
Muthianwala | JT - 406 |  | Submersible | 17.2753 | 28.4181 | 9.3961 | 51.2557 | 17.2753 | 28.4181 | 60
Muthianwala | R2 - 314 | 7.5 | Submersible | 10.8706 | 26.2009 | 9.5602 | 29.2261 | 10.8706 | 26.2009 | 62.4
Muthianwala | JB - 393 | 5 | Submersible | 16.5606 | 23.9744 | 7.7111 | 50.5097 | 16.5606 | 23.9744 | 62.4
Muthianwala | JB - 1135 | 7.5 | Submersible | 18.1562 | 19.938 | 8.0152 | 44.3056 | 18.1562 | 19.938 | 59.28
Muthianwala | JB - 841 | 7.5 | Submersible | 16.6657 | 20.9937 | 7.445 | 46.1018 | 16.6657 | 20.9937 | 59.28
Muthianwala | JB - 108 | 7.5 | Submersible | 17.7054 | 29.1923 | 9.7311 | 52.105 | 17.7054 | 29.1923 | 60
Muthianwala | JB - 188 | 7.5 | Submersible | 20.7351 | 27.0433 | 9.1556 | 60.082 | 20.7351 | 27.0433 | 60
Muthianwala | JB - 928 | 7.5 | Submersible | 14.5336 | 32.6323 | 8.5899 | 54.1631 | 14.5336 | 32.6323 | 64
Muthianwala | JB - 142 | 7.5 | Submersible | 13.2777 | 19.6249 | 5.8035 | 44.0463 | 13.2777 | 19.6249 | 59.28
Muthianwala | JB - 966 | 7.5 | Submersible | 13.6536 | 26.7698 | 7.4626 | 48.0475 | 13.6536 | 26.7698 | 62.4
Muthianwala | JB -711 | 7.5 | Submersible | 14.1093 | 26.3158 | 8.6869 | 41.9301 | 14.1093 | 26.3158 | 62.4
Muthianwala | JB -18 | 7.5 | Submersible | 15.8713 | 12.0822 | 6.9885 | 26.9177 | 15.8713 | 12.0822 | 57
Muthianwala | JB - 428 | 7.5 | Submersible | 14.2937 | 17.9211 | 4.7996 | 52.3573 | 14.2937 | 17.9211 | 60
Muthianwala | JB - 828 | 7.5 | Submersible | 13.8411 | 24.3572 | 8.771 | 37.7067 | 13.8411 | 24.3572 | 62.4
Muthianwala | JB - 205 | 7.5 | Submersible | 14.4376 | 27.4641 | 9.345 | 41.6244 | 14.4376 | 27.4641 | 60.8
Muthianwala | Jb - 327 | 7.5 | Submersible | 14.7246 | 27.1739 | 7.2811 | 53.9103 | 14.7246 | 27.1739 | 62.4
Muthianwala | JB - 528 | 7.5 | Submersible | 13.6034 | 22.2717 | 8.0323 | 37.0022 | 13.6034 | 22.2717 | 62.4
Muthianwala | New Connection | 7.5 | Submersible | 13.8314 | 25.2525 | 7.4937 | 45.7241 | 13.8314 | 25.2525 | 62.4
Muthianwala | JB - 745 | 7.5 | Submersible | 13.8777 | 21.7496 | 7.7788 | 38.0649 | 13.8777 | 21.7496 | 62.4
Muthianwala | R2 - 262 | 7.5 | Monoblock | 9.6337 | 5.2319 | 6.7003 | 7.3796 | 9.6337 | 5.2319 | 60
Muthianwala | R2 - 257 | 7.5 | Submersible | 10.3212 | 30.581 | 9.3681 | 33.0523 | 10.3212 | 30.581 | 64
Muthianwala | G - 114 | 7.5 | Submersible | 12.0539 | 24.0577 | 9.1398 | 31.1255 | 12.0539 | 24.0577 | 62.4
Muthianwala | New Connection | 7.5 | Submersible | 8.5345 | 27.4725 | 5.4786 | 41.9834 | 8.5345 | 27.4725 | 62.4
Muthianwala | New Connection | 7.5 | Monoblock | 8.3465 | 23.8347 | 6.6297 | 29.4369 | 8.3465 | 23.8347 | 62.4
Muthianwala | JB - 1043 | 7.5 | Submersible | 14.9937 | 16.0371 | 6.9054 | 34.1598 | 14.9937 | 16.0371 | 60
Muthianwala | G - 188 | 7.5 | Monoblock | 10.0415 | 26.5174 | 6.0115 | 43.4522 | 10.0415 | 26.5174 | 62.4
Muthianwala | JB - 160 | 7.5 | Submersible | 16.8905 | 27.6074 | 8.3473 | 54.8011 | 16.8905 | 27.6074 | 62.4
Muthianwala | R - 315 | 7.5 | Submersible | 17.3735 | 28.8277 | 10.2926 | 47.7354 | 17.3735 | 28.8277 | 58.5
Muthianwala | JB - 1297 | 5 | Submersible | 17.137 | 16.2162 | 6.7984 | 40.1003 | 17.137 | 16.2162 | 60
Muthianwala | R - 246 | 7.5 | Submersible | 16.7152 | 25.3022 | 9.1418 | 45.3846 | 16.7152 | 25.3022 | 60.8
Muthianwala | R - 95 | 7.5 | Submersible | 17.9063 | 35.461 | 11.3901 | 54.6887 | 17.9063 | 35.461 | 58.5
Muthianwala | R - 211 | 7.5 | Submersible | 17.6608 | 32.0399 | 12.73 | 43.6057 | 17.6608 | 32.0399 | 58.5
Muthianwala | JB - 706 | 12.5 | Submersible | 14.9181 | 33.4946 | 10.736 | 45.658 | 14.9181 | 33.4946 | 64
Muthianwala | G - 230 | 7.5 | Submersible | 16.5746 | 24.187 | 8.1271 | 48.3902 | 16.5746 | 24.187 | 58.52
Muthianwala | New Connection | 7.5 | Submersible | 14.8691 | 18.5759 | 5.2804 | 51.3136 | 14.8691 | 18.5759 | 58.52
Muthianwala | JB - 586 | 7.5 | Submersible | 14.2232 | 29.6834 | 8.349 | 49.6074 | 14.2232 | 29.6834 | 64
Muthianwala | JB - 254 | 7.5 | Submersible | 14.0195 | 27.1248 | 7.6317 | 48.8813 | 14.0195 | 27.1248 | 62.4
Muthianwala | JB - 1079 | 7.5 | Submersible | 14.29 | 30.3746 | 9.3588 | 45.4982 | 14.29 | 30.3746 | 64
Muthianwala | JB - 686 | 5 | Submersible | 13.5179 | 25.1467 | 8.3952 | 39.722 | 13.5179 | 25.1467 | 62.4
Muthianwala | JB - 793 | 7.5 | Submersible | 14.3216 | 30.6958 | 10.006 | 43.1002 | 14.3216 | 30.6958 | 64
Muthianwala | JB - 346 | 7.5 | Submersible | 13.7553 | 24.2981 | 6.6405 | 49.3753 | 13.7553 | 24.2981 | 62.4
Muthianwala | G - 43 | 7.5 | Submersible | 15.8216 | 20.1568 | 8.7656 | 35.6911 | 15.8216 | 20.1568 | 58.52
Muthianwala | G - 46 | 7.5 | Submersible | 13.1178 | 19.5908 | 6.002 | 42.0037 | 13.1178 | 19.5908 | 58.5
Muthianwala | R2 - 220 | 7.5 | Submersible | 13.5358 | 18.7188 | 7.2108 | 34.4706 | 13.5358 | 18.7188 | 58.5
Muthianwala | G - 103 | 7.5 | Submersible | 13.5609 | 20.9692 | 7.1182 | 39.1896 | 13.5609 | 20.9692 | 58.5
Muthianwala | G - 80 | 7.5 | Submersible | 13.5876 | 19.4595 | 7.1089 | 36.4871 | 13.5876 | 19.4595 | 58.5
Muthianwala | G - 153 | 7.5 | Submersible | 14.5919 | 17.5063 | 5.4308 | 46.1438 | 14.5919 | 17.5063 | 60
Muthianwala | G - 227 | 7.5 | Submersible | 15.4605 | 19.5355 | 7.1811 | 41.2597 | 15.4605 | 19.5355 | 59.28
Muthianwala | G - 63 | 7.5 | Submersible | 13.4232 | 18.9633 | 6.2622 | 39.8758 | 13.4232 | 18.9633 | 58.5
Muthianwala | New Connection | 7.5 | Submersible | 14.1116 | 19.595 | 8.5741 | 31.6377 | 14.1116 | 19.595 | 59.28
Muthianwala | JB - 164 | 7.5 | Submersible | 14.6729 | 24.032 | 7.252 | 47.7001 | 14.6729 | 24.032 | 62.4
Muthianwala | JB - 387 | 7.5 | Submersible | 13.9005 | 22.0696 | 6.1206 | 49.1703 | 13.9005 | 22.0696 | 62.4
Muthianwala | JB - 650 | 7.5 | Submersible | 14.5145 | 22.1293 | 6.158 | 51.1678 | 14.5145 | 22.1293 | 62.4
Muthianwala | JB - 1133 | 7.5 | Submersible | 13.9999 | 25.395 | 9.6564 | 36.1181 | 13.9999 | 25.395 | 60.8
Muthianwala | R2 - 109 | 7.5 | Submersible | 13.2146 | 20.6327 | 9.8119 | 27.2599 | 13.2146 | 20.6327 | 58.5
Muthianwala | R2 - 281 | 7.5 | Submersible | 13.9322 | 24.1352 | 11.2001 | 29.452 | 13.9322 | 24.1352 | 62.4
Muthianwala | R2 - 257 | 7.5 | Monoblock | 9.697 | 24.4765 | 5.9847 | 38.9061 | 9.697 | 24.4765 | 62.4
Muthianwala | R2 - 91 | 7.5 | Monoblock | 11.8292 | 22.4439 | 5.64 | 46.1792 | 11.8292 | 22.4439 | 58.5
Muthianwala | AP06/0949 | 7.5 | Monoblock | 11.2941 | 17.3177 | 5.2534 | 36.5234 | 11.2941 | 17.3177 | 60
Muthianwala | G - 266 | 7.5 | Monoblock | 6.5343 | 27.6923 | 8.0574 | 22.0308 | 6.5343 | 27.6923 | 62.4
Muthianwala | G - 71 | 7.5 | Monoblock | 8.4232 | 12.7841 | 4.3981 | 24.0187 | 8.4232 | 12.7841 | 57
Muthianwala | JB - 158 | 7.5 | Submersible | 8.1291 | 24.2718 | 9.577 | 20.2109 | 8.1291 | 24.2718 | 62.4
Muthianwala | G - 238 | 7.5 | Submersible | 11.1728 | 27.0921 | 11.2975 | 26.2839 | 11.1728 | 27.0921 | 62.4
Muthianwala | G - 24 | 7.5 | Submersible | 14.0937 | 25.3093 | 9.2086 | 38 | 14.0937 | 25.3093 | 60.8
Muthianwala | G - 5 | 7.5 | Submersible | 12.2247 | 31.881 | 8.1366 | 46.989 | 12.2247 | 31.881 | 62.4
Muthianwala | G - 133 | 7.5 | Submersible | 10.9961 | 23.7029 | 9.3947 | 27.2163 | 10.9961 | 23.7029 | 62.4
Muthianwala | G - 127 | 7.5 | Submersible | 8.9006 | 20.2977 | 10.7207 | 16.5314 | 8.9006 | 20.2977 | 58.5
Muthianwala | G - 205 | 7.5 | Submersible | 10.9464 | 25.8028 | 10.0488 | 27.5735 | 10.9464 | 25.8028 | 62.4
Muthianwala | JB - 643 | 5 | Submersible | 9.8389 | 17.081 | 5.2863 | 31.1872 | 9.8389 | 17.081 | 58.5
Muthianwala | G - 291 | 7.5 | Submersible | 10.4914 | 23.7154 | 8.0833 | 30.1954 | 10.4914 | 23.7154 | 62.4
Muthianwala | JB - 57 | 7.5 | Submersible | 14.0794 | 24.91 | 8.877 | 38.7581 | 14.0794 | 24.91 | 60.8
Muthianwala | JB - 240 | 7.5 | Submersible | 14.0272 | 24.4632 | 10.6557 | 31.5916 | 14.0272 | 24.4632 | 60.8
Muthianwala | JB - 967 | 7.5 | Submersible | 14.2788 | 26.7221 | 9.68 | 38.6685 | 14.2788 | 26.7221 | 60.8
Muthianwala | R2 - 140 | 7.5 | Monoblock | 10.0841 | 4.6392 | 3.7532 | 12.2278 | 10.0841 | 4.6392 | 57
Muthianwala | R - 22 | 7.5 | Submersible | 17.2943 | 31.3261 | 9.4339 | 56.3361 | 17.2943 | 31.3261 | 62.4
Muthianwala | R - 309 | 5 | Submersible | 15.9517 | 15.7535 | 8.7316 | 28.2331 | 15.9517 | 15.7535 | 60
Muthianwala | R - 301 | 7.5 | Submersible | 16.3212 | 16.5229 | 9.6684 | 27.3621 | 16.3212 | 16.5229 | 60
Muthianwala | R - 312 | 7.5 | Submersible | 17.886 | 34.5888 | 10.3972 | 58.3713 | 17.886 | 34.5888 | 62.4
Muthianwala | R - 308 | 5 | Submersible | 17.3316 | 32.9308 | 9.1586 | 61.1338 | 17.3316 | 32.9308 | 62.4
Muthianwala | JB - 1055 | 5 | Submersible | 14.8873 | 18.3936 | 8.8253 | 30.4384 | 14.8873 | 18.3936 | 58.5
Muthianwala | JB - 437 | 5 | Submersible | 13.5997 | 21.3321 | 7.285 | 39.0661 | 13.5997 | 21.3321 | 58.5
Muthianwala | JB - 362 | 7.5 | Submersible | 13.8557 | 23.4497 | 8.8471 | 36.0276 | 13.8557 | 23.4497 | 58.5
Muthianwala |  | 5 | Submersible | 13.5408 | 19.9115 | 6.3944 | 41.3636 | 13.5408 | 19.9115 | 58.5
Muthianwala | JB - 670 | 5 | Submersible | 15.6407 | 21.4643 | 6.1222 | 53.7942 | 15.6407 | 21.4643 | 62.4
Muthianwala | JB - 517 | 5 | Submersible | 13.7798 | 23.3524 | 6.8501 | 46.0837 | 13.7798 | 23.3524 | 62.4
Muthianwala | JB - 1068 | 7.5 | Submersible | 13.6515 | 11.5666 | 11.6986 | 13.2411 | 13.6515 | 11.5666 | 56.25
Muthianwala | G - 173 | 7.5 | Submersible | 14.2196 | 14.8173 | 4.83 | 42.7935 | 14.2196 | 14.8173 | 60
Muthianwala | New Connection | 10 | Submersible | 13.4508 | 10.057 | 5.0885 | 26.0795 | 13.4508 | 10.057 | 56.25
Muthianwala | New Connection | 10 | Submersible | 13.8788 | 24.9931 | 8.4068 | 40.4774 | 13.8788 | 24.9931 | 62.4
Muthianwala | G - 42 | 7.5 | Submersible | 13.7705 | 20.1748 | 7.5495 | 36.1005 | 13.7705 | 20.1748 | 58.5
Muthianwala | JB - 344 | 7.5 | Submersible | 13.9823 | 23.1839 | 7.0979 | 44.8026 | 13.9823 | 23.1839 | 62.4
Muthianwala | JB - 770 | 7.5 | Submersible | 14.0421 | 19.578 | 5.306 | 50.8277 | 14.0421 | 19.578 | 58.5
Muthianwala | JB - 159 | 7.5 | Submersible | 11.9504 | 13.7868 | 5.3178 | 30.3938 | 11.9504 | 13.7868 | 56.25
Muthianwala | JB - 165 | 7.5 | Submersible | 13.7299 | 19.544 | 9.8202 | 26.8057 | 13.7299 | 19.544 | 58.5
Muthianwala | G - 717 | 7.5 | Submersible | 13.3741 | 18.8048 | 5.8678 | 42.0465 | 13.3741 | 18.8048 | 58.5
Muthianwala | G - 254 | 7.5 | Submersible | 13.7125 | 19.2678 | 5.9879 | 43.2856 | 13.7125 | 19.2678 | 58.5
Muthianwala | G - 144 | 7.5 | Submersible | 14.0274 | 19.3465 | 5.8496 | 45.5113 | 14.0274 | 19.3465 | 58.5
Muthianwala | G - 3 | 7.5 | Submersible | 14.0528 | 23.4192 | 6.8307 | 47.2653 | 14.0528 | 23.4192 | 62.4
Muthianwala | R2 - 143 | 7.5 | Submersible | 14.8519 | 31.337 | 10.8116 | 42.23 | 14.8519 | 31.337 | 62.4
Muthianwala | R2 - 150 | 10 | Submersible | 14.6184 | 29.0604 | 12.2449 | 34.0341 | 14.6184 | 29.0604 | 62.4
Muthianwala | R2 - 117 | 7.5 | Submersible | 12.1886 | 22.2827 | 6.9398 | 38.3924 | 12.1886 | 22.2827 | 62.4
Muthianwala | JB - 1008 | 7.5 | Submersible | 12.9037 | 29.2493 | 8.8591 | 41.7934 | 12.9037 | 29.2493 | 62.4
Muthianwala | JB - 131 | 7.5 | Submersible | 14.3177 | 25.8844 | 8.7316 | 41.6377 | 14.3177 | 25.8844 | 60.8
Muthianwala | G - 228 | 7.5 | Submersible | 12.1824 | 22.0426 | 7.6376 | 34.4912 | 12.1824 | 22.0426 | 58.5
Muthianwala | JT - 340 | 7.5 | Submersible | 12.1321 | 22.0372 | 9.6793 | 27.0967 | 12.1321 | 22.0372 | 58.5
Muthianwala | G - 239 | 7.5 | Submersible | 13.4169 | 31.6456 | 8.8146 | 47.253 | 13.4169 | 31.6456 | 62.4
Muthianwala | JB - 75 | 7.5 | Submersible | 17.0449 | 21.5363 | 7.7572 | 46.4223 | 17.0449 | 21.5363 | 58.52
Muthianwala | R2 - 306 | 7.5 | Submersible | 14.3648 | 14.2721 | 5.7778 | 34.8095 | 14.3648 | 14.2721 | 58.5
Muthianwala | G - 131 | 7.5 | Submersible | 10.8614 | 25.9291 | 8.9848 | 30.7491 | 10.8614 | 25.9291 | 62.4
Muthianwala | New Connection | 10 | Submersible | 13.5946 | 21.3472 | 8.8335 | 32.229 | 13.5946 | 21.3472 | 59.28
Muthianwala | G - 137 | 3 | Submersible | 15.9562 | 21.9191 | 8.5467 | 40.1444 | 15.9562 | 21.9191 | 58.52
Muthianwala | JB - 250 | 5 | Submersible | 13.3614 | 17.0648 | 5.6056 | 39.9025 | 13.3614 | 17.0648 | 60
Muthianwala | JB - 1118 | 7.5 | Submersible | 14.7916 | 32.7154 | 14.5458 | 32.6362 | 14.7916 | 32.7154 | 62.4
Muthianwala | JB - 561 | 7.5 | Submersible | 13.5668 | 20.1117 | 6.9785 | 38.3561 | 13.5668 | 20.1117 | 58.5
Muthianwala | JB - 574 | 7.5 | Submersible | 13.7487 | 23.0651 | 8.1369 | 38.2321 | 13.7487 | 23.0651 | 62.4
Muthianwala | JB - 750-A | 10 | Submersible | 14.2188 | 27.4977 | 9.8355 | 38.9969 | 14.2188 | 27.4977 | 60.8
Muthianwala | JB - 558 | 7.5 | Submersible | 13.9106 | 25.1607 | 7.9791 | 43.0314 | 13.9106 | 25.1607 | 62.4
Muthianwala | JB - 831 | 7.5 | Submersible | 14.5304 | 30.9491 | 8.3482 | 52.845 | 14.5304 | 30.9491 | 62.4
Muthianwala | New Connection | 7.5 | Submersible | 13.5811 | 16.3636 | 7.9678 | 27.3619 | 13.5811 | 16.3636 | 60
Muthianwala | G - 225 | 7.5 | Submersible | 13.1712 | 20.2475 | 8.83 | 29.6282 | 13.1712 | 20.2475 | 58.5
Muthianwala | JB - 927 | 7.5 | Submersible | 12.9899 | 17.1559 | 6.9325 | 31.5357 | 12.9899 | 17.1559 | 60
Muthianwala | G - 106 | 7.5 | Submersible | 13.4272 | 23.898 | 9.1674 | 34.3376 | 13.4272 | 23.898 | 62.4
Muthianwala | G - 75 | 7.5 | Submersible | 13.2843 | 21.797 | 8.9095 | 31.8825 | 13.2843 | 21.797 | 58.5
Muthianwala | G - 167 | 7.5 | Submersible | 13.604 | 24.1222 | 10.6637 | 30.1887 | 13.604 | 24.1222 | 62.4
Muthianwala | New Connection | 7.5 | Submersible | 10.6789 | 31.8246 | 9.2362 | 36.0966 | 10.6789 | 31.8246 | 62.4
Muthianwala | New Connection | 7.5 | Submersible | 10.6654 | 34.5755 | 10.0508 | 35.9927 | 10.6654 | 34.5755 | 62.4
Muthianwala | G - 6 | 7.5 | Monoblock | 15.7141 | 31.4027 | 9.2893 | 52.1124 | 15.7141 | 31.4027 | 62.4
Muthianwala | G - 64 | 7.5 | Submersible | 12.5097 | 29.2969 | 10.1058 | 35.5768 | 12.5097 | 29.2969 | 62.4
Muthianwala | G - 83 | 7.5 | Submersible | 13.6925 | 23.3827 | 7.1892 | 43.6884 | 13.6925 | 23.3827 | 62.4
Muthianwala | JB - 871 | 5 | Submersible | 13.7804 | 24.4101 | 12.0361 | 27.4167 | 13.7804 | 24.4101 | 62.4
Muthianwala | JB - 1007 | 5 | Submersible | 13.7851 | 24.4698 | 8.7094 | 37.9947 | 13.7851 | 24.4698 | 62.4
Muthianwala | JB - 581 | 5 | Submersible | 16.3371 | 23.9553 | 8.2328 | 46.6337 | 16.3371 | 23.9553 | 57
Muthianwala | JB - 1121 | 5 | Submersible | 14.5977 | 12.8041 | 3.6092 | 50.8029 | 14.5977 | 12.8041 | 56.25
Muthianwala | JB - 1124 | 7.5 | Submersible | 10.9962 | 14.2203 | 3.4984 | 43.8482 | 10.9962 | 14.2203 | 56.25
Muthianwala | JB - 878 | 5 | Submersible | 12.048 | 25.8102 | 5.6925 | 53.5881 | 12.048 | 25.8102 | 62.4
Muthianwala | JB - 849 | 7.5 | Submersible | 13.6613 | 21.8872 | 5.9783 | 49.0649 | 13.6613 | 21.8872 | 62.4
Muthianwala | JB - 418 | 7.5 | Submersible | 13.6844 | 23.178 | 10.4578 | 29.7528 | 13.6844 | 23.178 | 62.4
Muthianwala | JB - 618 | 5 | Submersible | 13.9057 | 25.1046 | 5.7767 | 59.2838 | 13.9057 | 25.1046 | 62.4
Muthianwala | JJ - 869 | 7.5 | Submersible | 13.5312 | 21.1516 | 7.7513 | 36.2221 | 13.5312 | 21.1516 | 58.5
Muthianwala | JB -1139 | 7.5 | Submersible | 14.3937 | 28.454 | 8.1885 | 49.0656 | 14.3937 | 28.454 | 62.4
Muthianwala | JB - 227 | 7.5 | Submersible | 12.936 | 15.737 | 6.2185 | 32.1147 | 12.936 | 15.737 | 60
Muthianwala | G - 257 | 7.5 | Submersible | 14.2605 | 25.2738 | 6.2695 | 56.3948 | 14.2605 | 25.2738 | 62.4
Muthianwala | New Connection | 7.5 | Submersible | 13.8673 | 23.5787 | 7.0438 | 45.538 | 13.8673 | 23.5787 | 62.4
Muthianwala | New Connection | 7.5 | Submersible | 13.5794 | 21.6606 | 6.5668 | 43.9411 | 13.5794 | 21.6606 | 62.4
Muthianwala | R2 - 165 | 7.5 | Submersible | 10.9338 | 25.9665 | 8.2983 | 33.5634 | 10.9338 | 25.9665 | 62.4
Muthianwala | JB - 894 | 7.5 | Submersible | 11.563 | 28.9855 | 9.3634 | 35.1145 | 11.563 | 28.9855 | 62.4
Muthianwala | R2 - 107 | 7.5 | Submersible | 12.3989 | 35.489 | 10.9074 | 39.5752 | 12.3989 | 35.489 | 62.4
Muthianwala | JB - 267 | 7.5 | Submersible | 14.4205 | 28.3554 | 10.5989 | 37.8463 | 14.4205 | 28.3554 | 62.4
Muthianwala | R2 - 9 | 7.5 | Submersible | 14.3147 | 22.1839 | 7.8814 | 39.5261 | 14.3147 | 22.1839 | 62.4
Muthianwala | R2 - 59 | 10 | Submersible | 14.6217 | 30.5707 | 12.2172 | 35.8922 | 14.6217 | 30.5707 | 59.28
Muthianwala | R2 - 241 | 7.5 | Submersible | 13.6167 | 20.6849 | 8.2448 | 33.5131 | 13.6167 | 20.6849 | 58.5
Muthianwala | R2 - 251 |  | Submersible | 14.5844 | 31.0773 | 12.7212 | 34.952 | 14.5844 | 31.0773 | 62.4
Muthianwala | JB - 368 |  | Submersible | 13.7774 | 21.797 | 8.3356 | 35.3425 | 13.7774 | 21.797 | 58.52
Muthianwala | R2 - 106 | 7.5 | Submersible | 13.6685 | 18.3599 | 7.6816 | 32.0484 | 13.6685 | 18.3599 | 58.5
Muthianwala | JM - 1093 | 7.5 | Submersible | 13.6164 | 26.2238 | 9.1481 | 38.2909 | 13.6164 | 26.2238 | 62.4
Muthianwala | G - 256 | 7.5 | Monoblock | 7.7936 | 21.0477 | 6.5328 | 24.6325 | 7.7936 | 21.0477 | 58.5
Muthianwala | R2 - 161 | 7.5 | Monoblock | 7.9908 | 25.3521 | 4.5538 | 43.6418 | 7.9908 | 25.3521 | 58.5
Muthianwala | G - 189 | 7.5 | Monoblock | 7.8559 | 25.1467 | 6.3899 | 30.3284 | 7.8559 | 25.1467 | 58.5
Muthianwala | G2 - 265 | 7.5 | Monoblock | 9.4168 | 28.7908 | 7.4681 | 35.6139 | 9.4168 | 28.7908 | 60.8
Muthianwala | G - 73 | 7.5 | Monoblock | 8.5401 | 18.68 | 4.1032 | 38.1404 | 8.5401 | 18.68 | 60
Muthianwala | G - 297 | 7.5 | Monoblock | 8.5835 | 19.2184 | 4.0601 | 39.858 | 8.5835 | 19.2184 | 60
Muthianwala | New Connection | 7.5 | Monoblock | 7.2441 | 24.644 | 5.8149 | 30.118 | 7.2441 | 24.644 | 58.5
Muthianwala | New Connection | 7.5 | Monoblock | 8.8778 | 26.6272 | 5.0268 | 46.1325 | 8.8778 | 26.6272 | 58.5
Muthianwala | G - 171 | 7.5 | Monoblock | 8.4613 | 24.4698 | 10.7365 | 18.9178 | 8.4613 | 24.4698 | 62.4
Muthianwala | New Connection | 7.5 | Monoblock | 8.7464 | 22.7618 | 11.1552 | 17.5076 | 8.7464 | 22.7618 | 62.4
Muthianwala | G - 211 | 7.5 | Monoblock | 8.814 | 17.9964 | 8.6855 | 17.9157 | 8.814 | 17.9964 | 60
Muthianwala | G - 263 | 5 | Monoblock | 7.071 | 29.2969 | 7.4589 | 27.2453 | 7.071 | 29.2969 | 62.4
Muthianwala | G - 134 | 7.5 | Submersible | 10.6948 | 12.5874 | 5.1358 | 25.7138 | 10.6948 | 12.5874 | 58.5
Muthianwala | G - 165 | 7.5 | Monoblock | 9.7996 | 18.1123 | 4.6409 | 37.5186 | 9.7996 | 18.1123 | 60
Muthianwala | New Connection | 5 | Monoblock | 9.8763 | 20.8285 | 5.3766 | 37.533 | 9.8763 | 20.8285 | 58.5
Muthianwala | G - 151 | 7.5 | Monoblock | 12.8924 | 26.2774 | 6.8119 | 48.7882 | 12.8924 | 26.2774 | 62.4
Muthianwala | G - 253 | 7.5 | Monoblock | 9.8511 | 22.2772 | 4.7118 | 45.6907 | 9.8511 | 22.2772 | 58.5
Muthianwala | G - 152 | 7.5 | Submersible | 11.1097 | 24.4432 | 7.6793 | 34.6904 | 11.1097 | 24.4432 | 60.8
Muthianwala | G - 54 | 5 | Monoblock | 10.319 | 26.2085 | 7.9828 | 33.2349 | 10.319 | 26.2085 | 60.8
Muthianwala | G - 99 | 7.5 | Monoblock | 9.1272 | 18.1214 | 4.6828 | 34.6492 | 9.1272 | 18.1214 | 60
Muthianwala | New Connection | 7.5 | Monoblock | 8.5406 | 28.222 | 6.1619 | 38.3737 | 8.5406 | 28.222 | 62.4
Muthianwala | G - 203 | 7.5 | Monoblock | 8.3212 | 17.3712 | 8.0365 | 17.6448 | 8.3212 | 17.3712 | 60
Muthianwala | G - 232 | 7.5 | Monoblock | 8.1722 | 16.6605 | 6.4353 | 20.7552 | 8.1722 | 16.6605 | 60
Muthianwala | G - 241 | 7.5 | Monoblock | 8.5469 | 26.4862 | 8.2563 | 26.8973 | 8.5469 | 26.4862 | 62.4
Muthianwala | G - 288 | 7.5 | Monoblock | 8.6191 | 20.7756 | 5.4739 | 32.0912 | 8.6191 | 20.7756 | 58.5
Muthianwala | G - 66 | 7.5 | Monoblock | 9.7005 | 15.6277 | 4.3749 | 33.9932 | 9.7005 | 15.6277 | 60
Muthianwala | G - 307 | 7.5 | Monoblock | 8.0232 | 16.6482 | 5.3726 | 24.3894 | 8.0232 | 16.6482 | 60
Muthianwala | G - 300 | 7.5 | Monoblock | 8.8947 | 24.8139 | 5.266 | 41.1158 | 8.8947 | 24.8139 | 58.5
Muthianwala | S - 114 | 7.5 | Monoblock | 8.0877 | 13.0909 | 5.8043 | 17.8943 | 8.0877 | 13.0909 | 58.5
Muthianwala | New Connection | 7.5 | Monoblock | 8.6585 | 22.3214 | 5.8182 | 32.5867 | 8.6585 | 22.3214 | 58.5
Muthianwala | G - 290 | 7.5 | Monoblock | 8.6878 | 21.7286 | 4.7309 | 39.1443 | 8.6878 | 21.7286 | 58.5
Muthianwala | G - 125 | 7.5 | Monoblock | 9.3702 | 14.8075 | 4.6858 | 29.048 | 9.3702 | 14.8075 | 60
Muthianwala | G - 260 | 5 | Monoblock | 10.0915 | 25.9291 | 5.2899 | 48.5251 | 10.0915 | 25.9291 | 58.5
Muthianwala | G - 295 | 5 | Monoblock | 9.7726 | 20.4732 | 5.8377 | 33.6218 | 9.7726 | 20.4732 | 58.5
Muthianwala | G - 275 | 5 | Monoblock | 12.2045 | 23.1244 | 5.7122 | 48.4681 | 12.2045 | 23.1244 | 62.4
Muthianwala | New Connection | 5 | Monoblock | 10.2535 | 30.581 | 8.7938 | 34.9796 | 10.2535 | 30.581 | 62.4
Muthianwala | New Connection | 7.5 | Submersible | 12.5164 | 23.898 | 10.1939 | 28.7853 | 12.5164 | 23.898 | 57
Muthianwala | G - 53 | 3 | Monoblock | 11.7074 | 10.9716 | 4.7237 | 26.6758 | 11.7074 | 10.9716 | 56.25
Muthianwala | G - 264 | 5 | Monoblock | 11.8338 | 20.5152 | 6.602 | 36.074 | 11.8338 | 20.5152 | 58.5
Muthianwala | G - 164 | 7.5 | Submersible | 11.9317 | 24.3704 | 13.5539 | 21.046 | 11.9317 | 24.3704 | 62.4
Muthianwala | G - 60 | 7.5 | Monoblock | 12.0792 | 28.1602 | 8.8982 | 37.5007 | 12.0792 | 28.1602 | 62.4
Muthianwala | New Connection | 7.5 | Monoblock | 11.2904 | 18.53 | 5.7368 | 35.7751 | 11.2904 | 18.53 | 58.5
Muthianwala | New Connection | 7.5 | Monoblock | 11.9374 | 26.455 | 6.2406 | 49.6432 | 11.9374 | 26.455 | 62.4
Muthianwala | New Connection | 7.5 | Monoblock | 11.6048 | 31.1311 | 8.5492 | 41.4547 | 11.6048 | 31.1311 | 62.4
Muthianwala | G - 219 | 5 | Monoblock | 12.6038 | 35.447 | 8.793 | 49.8437 | 12.6038 | 35.447 | 62.4
Muthianwala | G - 274 | 5 | Monoblock | 11.1063 | 23.9298 | 5.6083 | 46.489 | 11.1063 | 23.9298 | 62.4
Muthianwala | G - 299 | 7.5 | Monoblock | 8.0129 | 20.5573 | 5.7231 | 28.2355 | 8.0129 | 20.5573 | 58.5
Muthianwala | G - 221 | 5 | Monoblock | 11.1885 | 16.158 | 3.8284 | 46.325 | 11.1885 | 16.158 | 60
Muthianwala | G - 86 | 7.5 | Monoblock | 11.6185 | 18.3824 | 4.7615 | 44.0023 | 11.6185 | 18.3824 | 60
Muthianwala | G - 159 | 7.5 | Monoblock | 8.5904 | 20.4638 | 5.0081 | 34.4346 | 8.5904 | 20.4638 | 58.5
Muthianwala | G - 196 | 5 | Monoblock | 8.125 | 15.4719 | 4.2519 | 29.0035 | 8.125 | 15.4719 | 60
Muthianwala | G - 280 | 3 | Monoblock | 9.2887 | 13.4068 | 4.8997 | 24.9336 | 9.2887 | 13.4068 | 58.5
Muthianwala | G - 132 | 5 | Monoblock | 8.2832 | 20.7326 | 5.2365 | 32.1722 | 8.2832 | 20.7326 | 58.5
Muthianwala | G - 281 | 5 | Monoblock | 9.0958 | 17.914 | 3.98 | 40.1621 | 9.0958 | 17.914 | 60
Muthianwala | New Connection | 3 | Monoblock | 8.6881 | 19.2761 | 4.8738 | 33.7093 | 8.6881 | 19.2761 | 58.5
Muthianwala | New Connection | 5 | Monoblock | 8.5551 | 19.7498 | 4.6678 | 35.5098 | 8.5551 | 19.7498 | 58.5
Muthianwala | New Connection | 5 | Submersible | 8.7512 | 16.331 | 6.5673 | 21.3481 | 8.7512 | 16.331 | 60
Muthianwala | G - 85 | 7.5 | Monoblock | 10.7606 | 28.5805 | 7.9733 | 37.8388 | 10.7606 | 28.5805 | 60.8
Muthianwala | G - 181 | 7.5 | Submersible | 11.9529 | 16.2396 | 5.5448 | 34.3421 | 11.9529 | 16.2396 | 60
Muthianwala | G - 95 | 7.5 | Submersible | 11.1709 | 36.4372 | 10.6143 | 37.6192 | 11.1709 | 36.4372 | 62.4
Muthianwala | G - 269 | 10 | Submersible | 11.7984 | 25.9217 | 9.5894 | 31.2869 | 11.7984 | 25.9217 | 62.4
Muthianwala | G - 76 | 7.5 | Submersible | 10.3249 | 26.1932 | 11.4498 | 23.1712 | 10.3249 | 26.1932 | 62.4
Muthianwala | G - 59 | 7.5 | Submersible | 11.9621 | 24.1287 | 9.9116 | 28.5671 | 11.9621 | 24.1287 | 62.4
Muthianwala | JB - 1090 | 7.5 | Submersible | 11.3328 | 26.4706 | 10.0528 | 29.2741 | 11.3328 | 26.4706 | 62.4
Muthianwala | G - 67 | 7.5 | Submersible | 10.5047 | 22.4048 | 10.4895 | 22.0109 | 10.5047 | 22.4048 | 62.4
Muthianwala | G - 202 | 7.5 | Submersible | 11.0405 | 26.1856 | 9.1472 | 31.0051 | 11.0405 | 26.1856 | 62.4
Muthianwala | G - 161 | 7.5 | Submersible | 10.9846 | 23.3645 | 10.5078 | 23.9606 | 10.9846 | 23.3645 | 62.4
Muthianwala | G - 104 | 7.5 | Submersible | 11.1196 | 26.178 | 10.5221 | 27.139 | 11.1196 | 26.178 | 62.4
Muthianwala | G - 31 | 7.5 | Submersible | 10.3064 | 17.3144 | 6.895 | 25.3891 | 10.3064 | 17.3144 | 58.5
Muthianwala | G - 143 | 7.5 | Submersible | 10.9366 | 25.0069 | 6.5855 | 40.7399 | 10.9366 | 25.0069 | 62.4
Muthianwala | G - 271 | 7.5 | Submersible | 10.9275 | 24.0128 | 9.574 | 26.8869 | 10.9275 | 24.0128 | 62.4
Muthianwala | R2 - 278 | 7.5 | Submersible | 13.4856 | 35.531 | 11.1288 | 42.2377 | 13.4856 | 35.531 | 62.4
Muthianwala | G - 139 | 7.5 | Submersible | 11.7171 | 16.3994 | 9.1785 | 20.5373 | 11.7171 | 16.3994 | 60
Muthianwala | R2 - 265 | 7.5 | Submersible | 12.4476 | 23.9617 | 8.2789 | 35.3427 | 12.4476 | 23.9617 | 62.4
Muthianwala | R2 - 320 | 7.5 | Submersible | 12.98 | 29.1262 | 10.995 | 33.7312 | 12.98 | 29.1262 | 62.4
Muthianwala | G - 176 | 7.5 | Submersible | 13.7254 | 33.6574 | 8.6691 | 52.2756 | 13.7254 | 33.6574 | 58.5
Muthianwala | New Connection | 7.5 | Submersible | 12.2303 | 23.9872 | 8.8807 | 32.4071 | 12.2303 | 23.9872 | 62.4
Muthianwala | G - 191 | 7.5 | Submersible | 11.3166 | 30.9385 | 12.5672 | 27.3304 | 11.3166 | 30.9385 | 62.4
Muthianwala | G - 302 | 7.5 | Submersible | 12.9529 | 28.9017 | 11.1787 | 32.8524 | 12.9529 | 28.9017 | 62.4
Muthianwala | G - 55 | 7.5 | Submersible | 12.1597 | 22.7964 | 8.2719 | 32.8739 | 12.1597 | 22.7964 | 62.4
Muthianwala | JB - 365 | 10 | Submersible | 12.4125 | 26.285 | 10.71 | 29.8846 | 12.4125 | 26.285 | 62.4
Muthianwala | G - 148 | 7.5 | Submersible | 12.5436 | 21.8235 | 11.627 | 23.0965 | 12.5436 | 21.8235 | 58.5
Muthianwala | G - 146 | 7.5 | Submersible | 12.2396 | 24.3375 | 10.1359 | 28.8305 | 12.2396 | 24.3375 | 62.4
Muthianwala | R2 - 201 | 7.5 | Submersible | 12.6982 | 26.0718 | 9.4026 | 34.5408 | 12.6982 | 26.0718 | 62.4
Muthianwala | R2 - 1 | 12.5 | Submersible | 13.7523 | 34.6821 | 11 | 42.5358 | 13.7523 | 34.6821 | 62.4
Muthianwala | JB - 386 | 7.5 | Submersible | 12.878 | 29.9501 | 10.5406 | 35.8964 | 12.878 | 29.9501 | 62.4
Muthianwala | New Connection | 7.5 | Submersible | 12.3576 | 24 | 9.2715 | 31.3807 | 12.3576 | 24 | 62.4
Muthianwala | JM - 804 | 7.5 | Submersible | 12.7558 | 25.6849 | 9.2037 | 34.9213 | 12.7558 | 25.6849 | 62.4
Muthianwala | JM - 1094 | 7.5 | Submersible | 12.6982 | 28.49 | 13.1707 | 26.9461 | 12.6982 | 28.49 | 62.4
Muthianwala | JM - 474 | 7.5 | Submersible | 12.5443 | 26.5879 | 10.2068 | 32.0559 | 12.5443 | 26.5879 | 62.4
Muthianwala | JT - 1084 | 7.5 | Submersible | 12.1258 | 21.7444 | 9.6065 | 26.9254 | 12.1258 | 21.7444 | 62.4
Muthianwala | JB - 983 | 7.5 | Submersible | 12.8045 | 26.8978 | 8.4192 | 40.1307 | 12.8045 | 26.8978 | 62.4
Muthianwala | G - 293 | 7.5 | Submersible | 12.1451 | 20.9448 | 7.5109 | 33.2241 | 12.1451 | 20.9448 | 58.5
Muthianwala | JB - 912 | 7.5 | Submersible | 11.9707 | 20.2384 | 6.7488 | 35.2157 | 11.9707 | 20.2384 | 58.5
Muthianwala | JB - 52 | 7.5 | Submersible | 12.9748 | 24.7253 | 6.9901 | 45.0224 | 12.9748 | 24.7253 | 62.4
Muthianwala | G - 207 | 5 | Monoblock | 10.4088 | 20.3989 | 5.2896 | 39.3783 | 10.4088 | 20.3989 | 58.5
Muthianwala | G - 155 | 5 | Monoblock | 12.3438 | 20.7326 | 6.1559 | 40.7828 | 12.3438 | 20.7326 | 58.5
Muthianwala | G - 100 | 7.5 | Monoblock | 10.2549 | 23.8284 | 5.4485 | 43.9971 | 10.2549 | 23.8284 | 62.4
Muthianwala | G - 248 | 5 | Monoblock | 10.7275 | 20.5479 | 5.4113 | 39.9606 | 10.7275 | 20.5479 | 58.5
Muthianwala | GS - 130 | 3 | Monoblock | 10.115 | 20.979 | 5.1597 | 40.3458 | 10.115 | 20.979 | 58.5
Muthianwala | G - 279 | 3 | Monoblock | 9.6015 | 13.6343 | 3.3472 | 38.3672 | 9.6015 | 13.6343 | 58.5

## Ramsinghwala
Feeder Name | Account No. | Connected HP / Sanctioned Demand | Type of Pump | Existing Pump Set Measured Parameters |  |  |  | Energy Efficient Pump Sets Parameters
|  |  |  | Total Head (m) | Flow (l/s) | Power (kW) | Efficiency (%) | Head (m) | Flow (l/s) | Efficiency (%)
Ramsinghwala | R2 - 49 | 7.5 | Monoblock | 10.0515 | 30.3951 | 6.6256 | 45.2351 | 10 | 28 | 59
Ramsinghwala | JM - 175 | 7.5 | Monoblock | 9.9111 | 20.9448 | 4.5418 | 44.8371 | 13.2 | 22 | 52
Ramsinghwala | R2 - 239 | 7.5 | Monoblock | 10.0504 | 25.0836 | 4.7536 | 52.0258 | 11.9 | 25 | 52
Ramsinghwala | R2 - 230 | 7.5 | Monoblock | 11.4239 | 22.3491 | 7.3171 | 34.2301 | 11.9 | 25 | 52
Ramsinghwala | R2 - 96 | 5 | Monoblock | 11.4275 | 22.4383 | 8.0825 | 31.122 | 13.2 | 22 | 52
Ramsinghwala | R2 - 124 | 7.5 | Monoblock | 12.6305 | 21.0773 | 7.4287 | 35.1551 | 13.2 | 22 | 52
Ramsinghwala | R2 - 214 | 5 | Monoblock | 11.2874 | 22.2442 | 4.6902 | 52.5153 | 13.2 | 22 | 52
Ramsinghwala | R2 - 57 | 5 | Monoblock | 9.6336 | 22.6187 | 6.2428 | 34.2408 | 13.2 | 22 | 52
Ramsinghwala | R2 - 148 | 5 | Monoblock | 5.2784 | 20.9595 | 5.87 | 18.4889 | 6 | 19 | 39
Ramsinghwala | R2 - 287 | 5 | Monoblock | 10.6044 | 24.2392 | 5.5111 | 45.7551 | 11.9 | 25 | 52
Ramsinghwala | JM - 289 | 7.5 | Submersible | 18.6683 | 26.8097 | 9.3259 | 52.6473 | 17 | 25 | 75
Ramsinghwala | JM - 383 | 7.5 | Submersible | 14.2421 | 28.463 | 6.4872 | 61.3012 | 14 | 25 | 80
Ramsinghwala | JM - 101 | 7.5 | Submersible | 13.3971 | 18.2704 | 6.3362 | 37.8966 | 13 | 19.4444 | 79
Ramsinghwala | JB - 325 | 7.5 | Submersible | 13.5928 | 20.1613 | 6.4275 | 41.8267 | 13 | 19.4444 | 79
Ramsinghwala | JM - 121 | 7.5 | Submersible | 14.8983 | 16.8571 | 9.6302 | 25.5832 | 14 | 16.6667 | 78
Ramsinghwala | JM - 1010 | 7.5 | Submersible | 12.9584 | 16.1377 | 3.8297 | 53.567 | 14 | 16.6667 | 78
Ramsinghwala | JM - 92 | 7.5 | Submersible | 13.6363 | 19.8851 | 7.9082 | 33.637 | 13 | 19.4444 | 79
Ramsinghwala | JM - 114 | 7.5 | Submersible | 13.768 | 22.4495 | 6.6643 | 45.4981 | 14 | 22.2222 | 79
Ramsinghwala | JM - 835 | 7.5 | Submersible | 13.6925 | 21.7077 | 8.5207 | 34.2209 | 14 | 22.2222 | 79
Ramsinghwala | JM - 1045 | 7.5 | Submersible | 13.9224 | 24.5365 | 6.0346 | 55.5328 | 14 | 25 | 80
Ramsinghwala | R2 - 183 | 7.5 | Submersible | 13.8953 | 24.5098 | 6.1246 | 54.5505 | 14 | 25 | 80
Ramsinghwala | JM - 1066 | 7.5 | Submersible | 14.4438 | 15.536 | 5.1925 | 42.3947 | 14 | 16.6667 | 78
Ramsinghwala | JM - 646 | 7.5 | Submersible | 13.9756 | 25.59 | 5.7332 | 61.1942 | 14 | 25 | 80
Ramsinghwala | JM - 184 | 7.5 | Submersible | 13.1823 | 14.2586 | 6.8877 | 26.7707 | 13 | 13.8889 | 79
Ramsinghwala | New Connection | 7.5 | Submersible | 13.5577 | 20.5997 | 9.531 | 28.7461 | 13 | 19.4444 | 79
Ramsinghwala | JM - 893 | 7.5 | Submersible | 13.5827 | 20.1748 | 7.4172 | 36.2432 | 13 | 19.4444 | 79
Ramsinghwala | JM - 162 | 7.5 | Submersible | 13.5467 | 20.2931 | 8.0135 | 33.6533 | 13 | 19.4444 | 79
Ramsinghwala | JM - 38 | 7.5 | Submersible | 13.7381 | 24.9307 | 8.3215 | 40.3767 | 14 | 25 | 80
Ramsinghwala | R2 - 313 |  | Submersible | 12.2458 | 28.0899 | 7.8633 | 42.9138 | 12 | 25.5556 | 80
Ramsinghwala | New Connection | 7.5 | Submersible | 13.9239 | 24.9238 | 8.9949 | 37.8484 | 14 | 25 | 80
Ramsinghwala | R2 - 120 | 7.5 | Submersible | 15.7789 | 23.9234 | 8.7855 | 42.1505 | 14 | 25 | 80
Ramsinghwala | R2 - 153 | 7.5 | Submersible | 13.5471 | 20.3758 | 5.6593 | 47.8487 | 13 | 19.4444 | 79
Ramsinghwala | JM - 284 | 7.5 | Submersible | 13.3719 | 20.2156 | 6.5584 | 40.4343 | 13 | 19.4444 | 79
Ramsinghwala | JM - 286 | 7.5 | Submersible | 13.7478 | 25.0417 | 6.5447 | 51.6035 | 13 | 23.6111 | 79
Ramsinghwala | JM - 146 | 7.5 | Submersible | 14.241 | 14.6056 | 6.829 | 29.8794 | 16 | 14.4444 | 78
Ramsinghwala | JM -123 | 7.5 | Submersible | 14.7283 | 17.7901 | 6.3523 | 40.4641 | 14 | 16.6667 | 78
Ramsinghwala | New Connection | 5 | Submersible | 12.2458 | 28.0899 | 7.8633 | 42.9138 | 12 | 25.5556 | 80
Ramsinghwala | New Connection | 5 | Monoblock | 7.0129 | 19.198 | 4.512 | 29.2721 | 7 | 18.5 | 43
Ramsinghwala | R2 - 33 | 5 | Monoblock | 6.5161 | 20.9644 | 3.8225 | 35.0586 | 7 | 18.5 | 43
Ramsinghwala | R2 - 225 | 7.5 | Monoblock | 8.563 | 18.1378 | 7.5922 | 20.0685 | 10 | 16 | 52.5
Ramsinghwala | G - 108 | 7.5 | Monoblock | 8.0484 | 27.5145 | 5.7002 | 38.1111 | 8 | 31 | 52
Ramsinghwala | G - 197 | 7.5 | Monoblock | 6.8797 | 14.6651 | 3.7789 | 26.1915 | 7 | 18.5 | 43
Ramsinghwala | G - 102 | 5 | Monoblock | 8.2089 | 26.178 | 6.6868 | 31.5263 | 8 | 23 | 42
Ramsinghwala | G - 147 | 5 | Monoblock | 7.0099 | 19.4259 | 3.5669 | 37.4517 | 7 | 18.5 | 43
Ramsinghwala | R2 - 304 | 7.5 | Monoblock | 9.0665 | 23.9362 | 5.0456 | 42.194 | 11.9 | 25 | 52
Ramsinghwala | R2 - 160 | 7.5 | Submersible | 17.6947 | 36.5112 | 10.7119 | 59.1658 | 19 | 36.1111 | 80
Ramsinghwala | G - 87 | 5 | Monoblock | 16.3412 | 17.9462 | 6.2622 | 45.9406 | 18 | 16 | 60
Ramsinghwala | R2 - 227 | 5 | Monoblock | 17.216 | 20.6659 | 7.0288 | 49.6563 | 18 | 22 | 61
Ramsinghwala | R2 - 151 | 5 | Monoblock | 16.5987 | 27.1985 | 5.9804 | 74.0558 | 18 | 28 | 58
Ramsinghwala | R2 - 292 | 7.5 | Monoblock | 17.0211 | 24.0256 | 9.4909 | 42.269 | 18 | 22 | 61
Ramsinghwala | R2 - 16 | 7.5 | Submersible | 17.2336 | 29.1545 | 7.0209 | 70.2027 | 17 | 25 | 75
Ramsinghwala | New Connection | 10 | Submersible | 16.5532 | 20.5855 | 7.6029 | 43.9678 | 16 | 19.4444 | 66
Ramsinghwala | R2 - 24 | 7.5 | Submersible | 10.9153 | 25.3664 | 6.762 | 40.1685 | 12 | 25.5556 | 80
Ramsinghwala | R2 - 100 | 7.5 | Submersible | 10.721 | 23.2318 | 7.9492 | 30.7373 | 12 | 22.0426 | 77
Ramsinghwala | R2 - 134 | 7.5 | Submersible | 10.8896 | 21.2064 | 7.3959 | 30.6306 | 12 | 22.0426 | 77
Ramsinghwala | R2 - 298 | 7.5 | Submersible | 10.9439 | 21.5724 | 6.088 | 38.0423 | 12 | 22.0426 | 77
Ramsinghwala | R2 - 256 | 7.5 | Submersible | 11.673 | 26.4395 | 8.8604 | 34.1707 | 12 | 25.5556 | 80
Ramsinghwala | R2 - 14 | 7.5 | Submersible | 10.2945 | 16.2133 | 6.5348 | 25.0559 | 10 | 16.1551 | 80
Ramsinghwala | R2 - 162 | 7.5 | Submersible | 10.5133 | 23.6593 | 6.6005 | 36.9684 | 10 | 23.7906 | 76
Ramsinghwala | New Connection | 7.5 | Submersible | 10.3902 | 22.6586 | 6.4631 | 35.7343 | 10 | 23.7906 | 76
Ramsinghwala | New Connection | 7.5 | Submersible | 10.4397 | 23.6967 | 5.6591 | 42.8843 | 10 | 23.7906 | 76
Ramsinghwala | R2 - 70 | 7.5 | Monoblock | 16.052 | 15.5952 | 5.6071 | 43.7973 | 18 | 16 | 60
Ramsinghwala | R1 - 170 | 7.5 | Monoblock | 15.5938 | 20.0535 | 6.515 | 47.0867 | 18 | 16 | 60
Ramsinghwala | R2 - 295 | 5 | Monoblock | 12.7265 | 16.6667 | 4.5828 | 45.4038 | 13.2 | 22 | 52
Ramsinghwala | R2 - 289 | 5 | Monoblock | 16.1519 | 19.2885 | 7.065 | 43.2594 | 18 | 22 | 61
Ramsinghwala | R2 - 303 | 5 | Monoblock | 16.8513 | 22.3825 | 7.1768 | 51.5562 | 18 | 22 | 61
Ramsinghwala | R2 - 52 | 7.5 | Submersible | 14.3962 | 21.8925 | 6.3318 | 48.8301 | 14 | 22.2222 | 79
Ramsinghwala | R2 - 112 | 7.5 | Submersible | 16.0213 | 24.0128 | 8.0782 | 46.7193 | 16 | 23.6111 | 79
Ramsinghwala | R2 - 1089 | 7.5 | Submersible | 13.5352 | 20.1342 | 7.0968 | 37.6707 | 13 | 19.4444 | 79
Ramsinghwala | R2 - 41 | 7.5 | Submersible | 13.4443 | 21.2917 | 8.9942 | 31.2215 | 13 | 19.4444 | 79
Ramsinghwala | R2 - 206 | 7.5 | Submersible | 13.8088 | 23.2558 | 7.6134 | 41.3785 | 13 | 23.6111 | 79
Ramsinghwala | R2 - 266 | 5 | Submersible | 13.367 | 20.1478 | 8.6374 | 30.5877 | 13 | 19.4444 | 79
Ramsinghwala | JB - 335 | 7.5 | Submersible | 14.4504 | 29.2398 | 7.732 | 53.6081 | 15.5 | 29.1667 | 80
Ramsinghwala | G - 141 | 7.5 | Submersible | 14.2862 | 27.0758 | 7.7851 | 48.7421 | 14 | 25 | 80
Ramsinghwala | R2 - 46 | 5 | Submersible | 16.3485 | 23.0415 | 8.2928 | 44.561 | 15 | 24.4444 | 80
Ramsinghwala | R2 - 233 | 5 | Submersible | 14.8794 | 17.5541 | 5.213 | 49.153 | 14 | 16.6667 | 78
Ramsinghwala | R2 - 114 | 7.5 | Submersible | 15.4438 | 17.0004 | 5.8303 | 44.1762 | 14 | 16.6667 | 78
Ramsinghwala | R2 - 231 | 7.5 | Monoblock | 12.8678 | 25.6703 | 6.1237 | 52.9167 | 13.2 | 22 | 52
Ramsinghwala | R2 - 176 | 7.5 | Submersible | 14.2222 | 30.02 | 7.7007 | 54.3897 | 15.5 | 29.1667 | 80
Ramsinghwala | R2 - 293 | 7.5 | Submersible | 13.2841 | 20.2566 | 7.5819 | 34.817 | 13 | 19.4444 | 79
Ramsinghwala | New Connection | 7.5 | Submersible | 14.1554 | 15.8172 | 6.2181 | 35.3239 | 14 | 16.6667 | 78
Ramsinghwala | New Connection | 7.5 | Submersible | 12.1155 | 23.6842 | 13.4312 | 20.9582 | 12 | 22.0426 | 77
Ramsinghwala | R2 - 101 | 7.5 | Submersible | 13.0273 | 28.4001 | 7.1789 | 50.5574 | 16 | 27.7778 | 77
Ramsinghwala | R2 - 297 | 7.5 | Submersible | 11.8096 | 21.7654 | 5.8706 | 42.9522 | 12 | 22.0426 | 77
Ramsinghwala | R2 - 237 | 7.5 | Submersible | 11.7443 | 20.8962 | 7.456 | 32.2892 | 12 | 22.0426 | 77
Ramsinghwala | R2 - 164 | 7.5 | Submersible | 11.6128 | 19.1002 | 4.7629 | 45.6848 | 13 | 19.4444 | 79
Ramsinghwala | R2 - 249 | 7.5 | Submersible | 13.2333 | 17.6471 | 8.6483 | 26.4896 | 13 | 19.4444 | 79
Ramsinghwala | R2 - 267 | 7.5 | Submersible | 15.4487 | 24.8825 | 6.2627 | 60.2135 | 14 | 25 | 80
Ramsinghwala | R2 - 06 | 7.5 | Submersible | 12.0284 | 24.5031 | 6.7473 | 42.852 | 12 | 25.5556 | 80
Ramsinghwala | R2 - 244 | 7.5 | Submersible | 12.1327 | 23.7969 | 7.0288 | 40.2965 | 12 | 25.5556 | 80
Ramsinghwala | JB - 959 | 7.5 | Submersible | 13.8054 | 20.7708 | 6.3542 | 44.2702 | 13 | 19.4444 | 79
Ramsinghwala | R2 - 238 | 7.5 | Monoblock | 10.4926 | 19.1939 | 6.4696 | 30.5378 | 10 | 16 | 52.5
Ramsinghwala | R2 - 73 | 7.5 | Submersible | 12.9859 | 16.6144 | 7.3422 | 28.8269 | 13 | 19.4444 | 79
Ramsinghwala | R2 - 126 | 7.5 | Submersible | 13.2117 | 20.1072 | 5.4336 | 47.9612 | 13 | 19.4444 | 79
Ramsinghwala | R2 - 186 | 7.5 | Submersible | 13.6079 | 24.43 | 7.5258 | 43.3337 | 13 | 23.6111 | 79
Ramsinghwala | R2 - 141 | 7.5 | Submersible | 13.8438 | 26.9058 | 6.6446 | 54.9922 | 13 | 23.6111 | 79
Ramsinghwala | R1 - 272 | 7.5 | Submersible | 13.4561 | 22.779 | 6.948 | 43.2775 | 13 | 23.6111 | 79
Ramsinghwala | R2 - 168 | 7.5 | Submersible | 13.6582 | 25.4525 | 8.6619 | 39.3713 | 13 | 23.6111 | 79
Ramsinghwala | R2 - 30 | 7.5 | Submersible | 14.9325 | 36.3343 | 9.6999 | 54.8718 | 14 | 33.3333 | 80
Ramsinghwala | R2 - 23 | 5 | Monoblock | 16.1033 | 26.3004 | 9.7665 | 42.5413 | 18 | 22 | 61
Ramsinghwala | G - 229 | 7.5 | Submersible | 12.9333 | 21.8076 | 7.6587 | 36.1269 | 12 | 22.0426 | 77
Ramsinghwala | R2 - 135 | 5 | Monoblock | 11.9016 | 24.5031 | 7.9926 | 35.794 | 12 | 24 | 62
Ramsinghwala | R2 - 45 | 7.5 | Submersible | 12.7095 | 29.4214 | 9.4689 | 38.7401 | 12 | 25.5556 | 80
Ramsinghwala | New Connection | 7.5 | Submersible | 12.6623 | 25.6483 | 7.3154 | 43.5517 | 12 | 25.5556 | 80
Ramsinghwala | R2 - 158 | 5 | Submersible | 12.8915 | 31.5016 | 7.2407 | 55.0202 | 15 | 30.5556 | 80
Ramsinghwala | New Connection | 5 | Submersible | 15.8866 | 27.6158 | 9.3159 | 46.1992 | 16 | 27.7778 | 77
Ramsinghwala | R2 - 1 0 |  | Submersible | 12.2333 | 24.2261 | 8.0336 | 36.1899 | 12 | 25.5556 | 80
Ramsinghwala | R2 - 56 |  | Submersible | 12.6999 | 29.2018 | 9.8124 | 37.0771 | 15.5 | 29.1667 | 80
Ramsinghwala | R2 - 13 |  | Submersible | 12.8498 | 30.8325 | 8.8987 | 43.6764 | 15 | 30.5556 | 80
Ramsinghwala | R2 - 139 |  | Submersible | 11.4119 | 16.3934 | 7.0096 | 26.1819 | 14 | 16.6667 | 78
Ramsinghwala | R2 - 184 | 7.5 | Submersible | 12.6667 | 29.2208 | 9.5301 | 38.1 | 15.5 | 29.1667 | 80
Ramsinghwala | R2 - 93 | 7.5 | Submersible | 13.1687 | 34.1038 | 11.4553 | 38.4598 | 15 | 30.5556 | 80
Ramsinghwala | R2 - 58 | 7.5 | Submersible | 13.2978 | 18.1892 | 7.6562 | 30.9919 | 13 | 19.4444 | 79
Ramsinghwala | R2 - 137 | 7.5 | Submersible | 12.3321 | 24.5365 | 7.0822 | 41.913 | 12 | 25.5556 | 80
Ramsinghwala | R2 - 282 | 7.5 | Submersible | 14.1654 | 30.4054 | 6.8229 | 61.9272 | 15.5 | 29.1667 | 80
Ramsinghwala | New Connection | 5 | Monoblock | 12.9589 | 22.7848 | 5.9804 | 48.4341 | 13.2 | 22 | 52
Ramsinghwala | R2 - 71 | 7.5 | Submersible | 13.3503 | 22.9826 | 6.937 | 43.3898 | 13 | 23.6111 | 79
Ramsinghwala | R2 - 226 | 7.5 | Submersible | 13.378 | 22.3325 | 7.0364 | 41.6531 | 13 | 23.6111 | 79
Ramsinghwala | R2 - 83 | 7.5 | Submersible | 13.2218 | 20.2497 | 6.6983 | 39.2118 | 13 | 19.4444 | 79
Ramsinghwala | New Connection | 7.5 | Submersible | 13.7335 | 27.5651 | 7.7579 | 47.8703 | 15 | 24.4444 | 80
Ramsinghwala | R2 - 245 | 7.5 | Submersible | 14.0766 | 29.8112 | 7.5117 | 54.8034 | 15.5 | 29.1667 | 80
Ramsinghwala | R2 - 127 | 5 | Submersible | 14.1778 | 15.7867 | 5.9925 | 36.6404 | 14 | 16.6667 | 78
Ramsinghwala | R2 - 42 | 7.5 | Submersible | 13.3872 | 22.4495 | 7.8438 | 37.5869 | 13 | 23.6111 | 79
Ramsinghwala | R2 - 280 | 7.5 | Submersible | 14.1111 | 30.2521 | 6.7322 | 62.2052 | 15.5 | 29.1667 | 80
Ramsinghwala | R2 - 131 | 7.5 | Submersible | 13.6498 | 21.7812 | 4.9317 | 59.1399 | 13 | 23.6111 | 79
Ramsinghwala | R2 - 94 | 7.5 | Submersible | 13.4111 | 23.6904 | 8.8136 | 35.3632 | 15 | 24.4444 | 80
Ramsinghwala | R2 - 274 | 7.5 | Submersible | 14.325 | 26.0718 | 5.5323 | 66.2265 | 15 | 24.4444 | 80
Ramsinghwala | R2 - 277 | 7.5 | Submersible | 14.0642 | 26.643 | 8.8825 | 41.3838 | 15 | 24.4444 | 80
Ramsinghwala | R2 - 20 | 7.5 | Submersible | 13.6409 | 21.7077 | 6.0084 | 48.3468 | 13 | 23.6111 | 79
Ramsinghwala | R2 - 132 | 7.5 | Submersible | 13.4322 | 23.012 | 7.0762 | 42.8523 | 13 | 23.6111 | 79
Ramsinghwala | R2 - 53 | 7.5 | Submersible | 13.5917 | 24.8071 | 9.684 | 34.1557 | 13 | 23.6111 | 79
Ramsinghwala | JM - 915 | 7.5 | Submersible | 13.8765 | 27.8552 | 6.5679 | 57.7337 | 15.5 | 29.1667 | 80
Ramsinghwala | JM - 760 | 7.5 | Submersible | 14.235 | 24.9931 | 7.6937 | 45.3638 | 15 | 24.4444 | 80
Ramsinghwala | JM - 224 | 7.5 | Submersible | 13.5034 | 23.6904 | 6.3269 | 49.6016 | 13 | 23.6111 | 79
Ramsinghwala | R2 - 253 |  | Submersible | 13.0618 | 36 | 7.2836 | 63.333 | 12 | 36.1111 | 80
Ramsinghwala | R2 - 169 |  | Submersible | 12.2918 | 23.968 | 8.1743 | 35.3561 | 12 | 22.0426 | 77
Ramsinghwala | JM - 154 |  | Submersible | 13.7194 | 23.7342 | 6.6054 | 48.3594 | 13 | 23.6111 | 79
Ramsinghwala | JM - 298 |  | Submersible | 12.3462 | 24.5098 | 6.2277 | 47.6668 | 12 | 25.5556 | 80
Ramsinghwala | JM - 1083 |  | Submersible | 12.5173 | 27.3723 | 8.5687 | 39.2262 | 12 | 25.5556 | 80
Ramsinghwala | R2 - 259 |  | Submersible | 11.8318 | 22.0534 | 5.4506 | 46.9623 | 12 | 22.0426 | 77
Ramsinghwala | R2 - 260 |  | Submersible | 11.9544 | 23.6718 | 6.0528 | 45.864 | 12 | 22.0426 | 77
Ramsinghwala | JM - 170 |  | Submersible | 11.8734 | 18.2815 | 4.8963 | 43.4898 | 12 | 22.0426 | 77
Ramsinghwala | R2 - 204 |  | Submersible | 13.9958 | 19.0034 | 5.202 | 50.1563 | 13 | 19.4444 | 79
Ramsinghwala | JJ - 296 |  | Submersible | 12.4028 | 26.2927 | 8.2828 | 38.6231 | 12 | 25.5556 | 80
Ramsinghwala | R2 - 103 |  | Submersible | 12.716 | 29.4889 | 5.8016 | 63.4059 | 12 | 25.5556 | 80
Ramsinghwala | R2 - 167 |  | Submersible | 12.6968 | 29.5372 | 6.5714 | 55.9861 | 12 | 25.5556 | 80
Ramsinghwala | R2- 37 |  | Submersible | 9.3961 | 30.2115 | 8.4436 | 32.9808 | 10 | 27.7778 | 75
Ramsinghwala | R2 - 196 |  | Monoblock | 11.7141 | 20.4732 | 6.3543 | 37.0252 | 12 | 24 | 62
Ramsinghwala | R2 - 177 | 7.5 | Submersible | 12.1001 | 21.8341 | 7.613 | 34.0439 | 12 | 22.0426 | 77
Ramsinghwala | R2 - 64 | 7.5 | Submersible | 11.5656 | 18.3076 | 7.3496 | 28.2623 | 12 | 18.0556 | 78
Ramsinghwala | JM - 640 | 7.5 | Submersible | 11.9853 | 23.9489 | 7.5232 | 37.4281 | 12 | 22.0426 | 77
Ramsinghwala | JM - 72 | 7.5 | Submersible | 11.9027 | 20.8962 | 5.6632 | 43.0844 | 12 | 22.0426 | 77
Ramsinghwala | JM - 669 | 7.5 | Submersible | 13.4203 | 11.8452 | 4.6205 | 33.7511 | 13 | 13.8889 | 79
Ramsinghwala | JM - 580 | 7.5 | Submersible | 14.93 | 17.9211 | 9.3775 | 27.9903 | 14 | 16.6667 | 78
Ramsinghwala | JM - 1111 | 7.5 | Submersible | 13.9876 | 14.6771 | 3.8044 | 52.9376 | 13 | 13.8889 | 79
Ramsinghwala | R2 - 156 | 7.5 | Submersible | 14.1757 | 23.7029 | 8.7736 | 37.5698 | 15 | 24.4444 | 80
Ramsinghwala | R2 - 171 | 7.5 | Submersible | 11.2588 | 30.171 | 8.9286 | 37.3224 | 12 | 25.5556 | 80
Ramsinghwala | JM - 96 | 7.5 | Submersible | 13.6469 | 25.5247 | 7.9579 | 42.9403 | 13 | 23.6111 | 79
Ramsinghwala | JM - 416 | 7.5 | Submersible | 13.0584 | 17.741 | 6.1891 | 36.7206 | 13 | 19.4444 | 79
Ramsinghwala | R2 - 159 | 5 | Monoblock | 13.7062 | 21.0231 | 8.8801 | 31.8323 | 14.5 | 19 | 58
Ramsinghwala | R2 - 179 | 7.5 | Submersible | 13.467 | 23.4375 | 7.9264 | 39.0636 | 13 | 23.6111 | 79
Ramsinghwala | R2 - 193 | 7.5 | Monoblock | 12.6266 | 20.9864 | 5.2441 | 49.5704 | 13.2 | 22 | 52
Ramsinghwala | JM - 814 | 5 | Monoblock | 13.473 | 19.1205 | 6.0178 | 41.9947 | 13.2 | 22 | 52
Ramsinghwala | R2 - 44 | 7.5 | Submersible | 15.0321 | 39.1645 | 11.2191 | 51.4783 | 17 | 39 | 79
Ramsinghwala | R2 - 154 | 7.5 | Monoblock | 13.2925 | 22.4663 | 5.7582 | 50.8769 | 13.2 | 22 | 52
Ramsinghwala | R2 - 285 | 7.5 | Submersible | 13.2849 | 21.9888 | 19.8174 | 14.4605 | 13 | 24 | 79
Ramsinghwala | R2 - 335 | 5 | Monoblock | 12.8574 | 19.1002 | 5.2477 | 45.9085 | 13.2 | 22 | 52
Ramsinghwala | R2 - 84 | 7.5 | Monoblock | 12.0192 | 26.0417 | 6.4258 | 47.7842 | 13.2 | 22 | 52
Ramsinghwala | New Connection | 7.5 | Submersible | 11.6026 | 17.2117 | 7.3818 | 26.5391 | 12 | 18 | 78
Ramsinghwala | R2 - 316 | 7.5 | Monoblock | 11.8717 | 26.0643 | 5.7747 | 52.565 | 13.2 | 22 | 52
Ramsinghwala | New Connection | 7.5 | Monoblock | 12.6056 | 36.0288 | 7.4287 | 59.9751 | 12 | 27 | 51
Ramsinghwala | JM - 64 |  | Submersible | 13.055 | 28.5081 | 10.8451 | 33.665 | 12 | 25.5556 | 80
Ramsinghwala | R2 - 51 |  | Submersible | 12.4755 | 25.8546 | 8.2658 | 38.2809 | 12 | 25.5556 | 80
Ramsinghwala | R2- 50 |  | Submersible | 13.1715 | 33.6574 | 7.542 | 57.6628 | 15.5 | 29.1667 | 80
Ramsinghwala | R2 - 92 |  | Submersible | 12.5409 | 27.7949 | 7.2629 | 47.0821 | 12 | 25.5556 | 80
Ramsinghwala | JM - 932 |  | Monoblock | 12.8239 | 30.3439 | 5.9908 | 63.7201 | 12 | 27 | 51
Ramsinghwala | R2 - 283 |  | Monoblock | 11.7339 | 20.9351 | 6.2466 | 38.5782 | 12 | 24 | 62
Ramsinghwala | JT - 935 |  | Monoblock | 12.7979 | 30.02 | 6.1596 | 61.1875 | 12 | 27 | 51

## Talwandi
Feeder Name | Account No. | Connected HP / Sanctioned Demand | Type of Pump | Existing Pump Set Measured Parameters |  |  |  | Energy Efficient Pump Sets Parameters
|  |  |  | Total Head (m) | Flow (l/s) | Power (kW) | Efficiency (%) | Head (m) | Flow (l/s) | Efficiency (%)
Talwandi | JM - 30 | 7.5 | Submersible | 14.3235 | 33.6574 | 9.4926 | 49.8215 | 14.3235 | 33.6574 | 64
Talwandi | JM - 1112 | 7.5 | Submersible | 14.3065 | 29.7915 | 7.8898 | 52.9944 | 14.3065 | 29.7915 | 58.5
Talwandi | JM - 390 | 7.5 | Submersible | 14.2108 | 29.1829 | 8.5667 | 47.4901 | 14.2108 | 29.1829 | 58.5
Talwandi | JM - 1099 | 7.5 | Submersible | 15.9386 | 22.67 | 7.4598 | 47.5167 | 15.9386 | 22.67 | 58.5
Talwandi | JM - 755 | 7.5 | Submersible | 14.5914 | 33.1736 | 8.9218 | 53.2241 | 14.5914 | 33.1736 | 60
Talwandi | JM - 1114 | 7.5 | Submersible | 14.3722 | 34.1038 | 8.3617 | 57.5044 | 14.3722 | 34.1038 | 60
Talwandi | G - 157 | 5 | Submersible | 13.4002 | 23.5973 | 6.9547 | 44.6028 | 13.4002 | 23.5973 | 62.4
Talwandi | JM - 499 | 7.5 | Submersible | 13.7623 | 24.2849 | 7.0204 | 46.702 | 13.7623 | 24.2849 | 62.4
Talwandi | JM - 120 | 7.5 | Submersible | 14.0591 | 27.7949 | 9.1789 | 41.7638 | 14.0591 | 27.7949 | 60.84
Talwandi | G - 248 | 7.5 | Submersible | 14.043 | 27.6158 | 7.4236 | 51.2475 | 14.043 | 27.6158 | 62.4
Talwandi | JM - 366 | 7.5 | Submersible | 15.3715 | 39.5952 | 11.6735 | 51.148 | 15.3715 | 39.5952 | 60
Talwandi | JM - 284 | 7.5 | Submersible | 15.7743 | 22.1729 | 9.1791 | 37.3804 | 15.7743 | 22.1729 | 56.25
Talwandi | JM - 130 | 7.5 | Submersible | 14.0892 | 27.1166 | 6.3784 | 58.7595 | 14.0892 | 27.1166 | 62.4
Talwandi | JM - 20 | 7.5 | Submersible | 13.8831 | 24.0128 | 11.3723 | 28.7574 | 13.8831 | 24.0128 | 62.4
Talwandi | JB - 473 |  | Submersible | 14.7702 | 33.284 | 12.3255 | 39.1281 | 14.7702 | 33.284 | 60
Talwandi | JM - 68 | 7.5 | Submersible | 13.6476 | 21.5466 | 7.8757 | 36.6278 | 13.6476 | 21.5466 | 58.5
Talwandi | JM - 1004 | 7.5 | Submersible | 13.8708 | 24.1416 | 8.0951 | 40.5803 | 13.8708 | 24.1416 | 60
Talwandi | JM - 905 | 7.5 | Submersible | 15.6907 | 20.7039 | 7.0324 | 45.3172 | 15.6907 | 20.7039 | 58.5
Talwandi | JM - 825 | 5 | Submersible | 13.5793 | 20.9741 | 6.0171 | 46.4349 | 13.5793 | 20.9741 | 58.5
Talwandi | GM - 934 | 7.5 | Submersible | 13.9296 | 25.1783 | 5.7014 | 60.3468 | 13.9296 | 25.1783 | 60
Talwandi | JM - 153 | 10 | Submersible | 13.8731 | 24.3506 | 7.2089 | 45.9712 | 13.8731 | 24.3506 | 62.4
Talwandi | JM - 183 | 7.5 | Submersible | 13.7112 | 13.6488 | 4.8623 | 37.7567 | 13.7112 | 13.6488 | 57.75
Talwandi | JM - 995 | 7.5 | Submersible | 13.7063 | 11.378 | 4.5932 | 33.3074 | 13.7063 | 11.378 | 56.25
Talwandi | New Connection |  | Submersible | 14.3288 | 15.0451 | 5.6694 | 37.3022 | 14.3288 | 15.0451 | 60
Talwandi | JT - 550 | 7.5 | Submersible | 13.3855 | 22.9709 | 6.7017 | 45.0089 | 13.3855 | 22.9709 | 62.4
Talwandi | New Connection | 7.5 | Submersible | 14.3235 | 16.7473 | 6.7201 | 35.0176 | 14.3235 | 16.7473 | 60
Talwandi | 44 - 65 | 12.5 | Submersible | 14.2854 | 30.4569 | 12.2416 | 34.8666 | 14.2854 | 30.4569 | 60
Talwandi | JT - 728 | 7.5 | Submersible | 13.1136 | 19.0436 | 9.5504 | 25.6517 | 13.1136 | 19.0436 | 56.25
Talwandi | 44 - 145 | 7.5 | Submersible | 13.2883 | 21.1615 | 6.601 | 41.7904 | 13.2883 | 21.1615 | 58.5
Talwandi | 44 - 997 | 7.5 | Submersible | 13.5127 | 12.7083 | 5.552 | 30.3423 | 13.5127 | 12.7083 | 57.75
Talwandi | 44 - 145 | 7.5 | Submersible | 14.1227 | 23.9872 | 7.3005 | 45.5211 | 14.1227 | 23.9872 | 62.4
Talwandi | JB - 570 | 7.5 | Submersible | 13.3047 | 21.4643 | 7.1439 | 39.2152 | 13.3047 | 21.4643 | 58.5
Talwandi | JT - 846 | 7.5 | Submersible | 13.1531 | 20.0579 | 7.8269 | 33.0669 | 13.1531 | 20.0579 | 58.5
Talwandi | JT - 779 | 7.5 | Submersible | 13.7591 | 19.8325 | 4.8918 | 54.7225 | 13.7591 | 19.8325 | 58.5
Talwandi | 44 - 1209 | 7.5 | Submersible | 13.269 | 20.9011 | 7.0782 | 38.4374 | 13.269 | 20.9011 | 58.5
Talwandi | 44 - 693 | 7.5 | Submersible | 13.2896 | 10.9237 | 4.1949 | 33.9486 | 13.2896 | 10.9237 | 56.25
Talwandi | 43 - G91 | 12.5 | Submersible | 14.0878 | 36.0577 | 16.9341 | 29.4271 | 14.0878 | 36.0577 | 60
Talwandi | 44 - 895 | 12.5 | Submersible | 12.2007 | 21.8659 | 13.8629 | 18.8785 | 12.2007 | 21.8659 | 57.75
Talwandi | 44 - 154 | 12.5 | Submersible | 13.6354 | 34.9786 | 13.5304 | 34.5803 | 13.6354 | 34.9786 | 60
Talwandi | 44 - 957 | 7.5 | Submersible | 11.771 | 16.1377 | 7.9961 | 23.3049 | 11.771 | 16.1377 | 60
Talwandi | 44 - 1890 | 10 | Submersible | 13.2824 | 24.0256 | 11.2637 | 27.7933 | 13.2824 | 24.0256 | 62.4
Talwandi | New Connection | 7.5 | Submersible | 12.8645 | 14.5185 | 6.1308 | 29.886 | 12.8645 | 14.5185 | 58.5
Talwandi | JT - 329 | 7.5 | Submersible | 12.4289 | 25.345 | 10.9154 | 28.311 | 12.4289 | 25.345 | 62.4
Talwandi | 43 - 692 | 12.5 | Submersible | 12.7708 | 24.5566 | 11.4709 | 26.82 | 12.7708 | 24.5566 | 62.4
Talwandi | 44 - 1191 | 7.5 | Submersible | 12.8519 | 28.8832 | 12.6822 | 28.7135 | 12.8519 | 28.8832 | 56.25
Talwandi | 44 - 675 | 5 | Submersible | 13.2436 | 15.6658 | 4.7508 | 42.8409 | 13.2436 | 15.6658 | 60
Talwandi | 44 - 416 | 5 | Submersible | 13.151 | 11.0674 | 4.1989 | 34.0044 | 13.151 | 11.0674 | 56.25
Talwandi | JT - 1173 | 7.5 | Monoblock | 12.7114 | 29.1829 | 9.5664 | 38.0398 | 12.7114 | 29.1829 | 60
Talwandi | G - 82 | 12.5 | Submersible | 13.3266 | 35.0604 | 17.8904 | 25.6202 | 13.3266 | 35.0604 | 64
Talwandi | JT - 271 | 7.5 | Submersible | 13.1378 | 28.1514 | 12.6822 | 28.6087 | 13.1378 | 28.1514 | 58.5
Talwandi | G - 81 | 12.5 | Monoblock | 12.6101 | 36.7047 | 7.936 | 57.2148 | 12.6101 | 36.7047 | 60
Talwandi | 44 - 455 | 10 | Submersible | 13.2883 | 21.1615 | 6.5994 | 41.8004 | 13.2883 | 25.7511 | 62.4
Talwandi | G - 209 | 5 | Submersible | 13.8961 | 25.8176 | 7.2552 | 48.5093 | 13.8961 | 25.8176 | 60
Talwandi | G - 8 | 5 | Submersible | 14.232 | 29.4022 | 9.6078 | 42.7259 | 14.232 | 29.4022 | 60
Talwandi | G - 45 | 7.5 | Submersible | 14.3912 | 32.6679 | 10.8104 | 42.6625 | 14.3912 | 32.6679 | 60
Talwandi | G - 77 | 5 | Submersible | 15.8205 | 22.2387 | 8.436 | 40.913 | 15.8205 | 22.2387 | 62.4
Talwandi | G - 377 | 7.5 | Submersible | 14.1585 | 28.4001 | 7.6041 | 51.8749 | 14.1585 | 28.4001 | 62.4
Talwandi | G - 81A | 5 | Monoblock | 13.3779 | 23.8537 | 5.4806 | 57.1202 | 13.3779 | 23.8537 | 62.4
Talwandi | G - 44 | 7.5 | Submersible | 13.9211 | 26.0567 | 9.3795 | 37.9387 | 13.9211 | 26.0567 | 62.4
Talwandi | G - 65 | 7.5 | Submersible | 14.2438 | 29.7717 | 9.2711 | 44.8715 | 14.2438 | 29.7717 | 60
Talwandi | G - 246 | 7.5 | Submersible | 14.6302 | 32.2004 | 11.5455 | 40.0281 | 14.6302 | 32.2004 | 60
Talwandi | G - 156 | 7.5 | Monoblock | 12.8708 | 20.9741 | 5.4196 | 48.8641 | 12.8708 | 20.9741 | 58.5
Talwandi | G - 233 | 7.5 | Monoblock | 12.5976 | 22.0318 | 6.6185 | 41.1381 | 12.5976 | 22.0318 | 62.4
Talwandi | G - 33 | 7.5 | Submersible | 14.6346 | 30.8325 | 10.2631 | 43.1298 | 14.6346 | 30.8325 | 60
Talwandi | 44 - 190 | 7.5 | Submersible | 12.2979 | 20.8623 | 8.6876 | 28.9709 | 12.2979 | 20.8623 | 58.5
Talwandi | 44 - 212 | 7.5 | Submersible | 12.4234 | 11.7233 | 7.6382 | 18.7054 | 12.4234 | 11.7233 | 56.25
Talwandi | New Connection | 7.5 | Submersible | 12.3429 | 21.5105 | 9.7954 | 26.5898 | 12.3429 | 21.5105 | 58.5
Talwandi | JT - 854 | 7.5 | Submersible | 12.1784 | 18.1087 | 8.1295 | 26.6121 | 12.1784 | 18.1087 | 60
Talwandi | JT - 1082 | 7.5 | Monoblock | 11.9259 | 23.1362 | 6.7419 | 40.1486 | 11.9259 | 23.1362 | 62.4
Talwandi | JT - 55 | 7.5 | Submersible | 13.0365 | 28.0636 | 10.6096 | 33.8279 | 13.0365 | 28.0636 | 62.4
Talwandi | JT - 328 | 7.5 | Submersible | 11.8974 | 19.1734 | 7.9597 | 28.1141 | 11.8974 | 19.1734 | 58.5
Talwandi | JT - 541 | 7.5 | Submersible | 12.5071 | 18.7931 | 7.651 | 30.1376 | 12.5071 | 18.7931 | 58.5
Talwandi | JM - 902 | 7.5 | Submersible | 13.1907 | 14.4161 | 5.2327 | 35.65 | 13.1907 | 14.4161 | 56.25
Talwandi | JM - 51 | 6 | Submersible | 13.9837 | 25.3879 | 7.4786 | 46.5687 | 13.9837 | 25.3879 | 62.4
Talwandi | JM - 442 | 5 | Submersible | 14.6682 | 16.5654 | 6.0489 | 39.4065 | 14.6682 | 16.5654 | 60
Talwandi | JM - 389 | 5 | Submersible | 13.28 | 16.1175 | 5.0345 | 41.7071 | 13.28 | 16.1175 | 60
Talwandi | JM - 123 | 7.5 | Submersible | 13.3832 | 17.783 | 12.0671 | 19.3479 | 13.3832 | 17.783 | 60
Talwandi | JM - 364 | 5 | Submersible | 13.2726 | 15.9915 | 4.7791 | 43.5675 | 13.2726 | 15.9915 | 60
Talwandi | JM - 1122 | 7.5 | Submersible | 13.7085 | 22.1457 | 7.3253 | 40.6558 | 13.7085 | 22.1457 | 62.4
Talwandi | JM - 27 | 7.5 | Submersible | 13.7995 | 23.1481 | 5.6653 | 55.3132 | 13.7995 | 23.1481 | 62.4
Talwandi | JM - 945 | 5 | Submersible | 13.4347 | 18.7696 | 7.621 | 32.4594 | 13.4347 | 18.7696 | 57.75
Talwandi | JT - 582 | 5 | Submersible | 15.3832 | 18.7813 | 5.1632 | 54.8937 | 15.3832 | 18.7813 | 58.5
Talwandi | JT - 1038 | 7.5 | Submersible | 12.393 | 25.4381 | 7.7384 | 39.9649 | 12.393 | 25.4381 | 62.4
Talwandi | JT - 1037 | 7.5 | Submersible | 12.0132 | 21.0674 | 7.8981 | 31.4353 | 12.0132 | 21.0674 | 58.5
Talwandi | JT - 229 | 7.5 | Submersible | 12.0221 | 16.266 | 6.0254 | 31.8378 | 12.0221 | 16.266 | 60
Talwandi | JT - 260 | 7.5 | Submersible | 12.4293 | 21.1665 | 8.42 | 30.6515 | 12.4293 | 21.1665 | 58.5
Talwandi | JT - 735 | 7.5 | Submersible | 12.5395 | 24.1416 | 7.1247 | 41.6822 | 12.5395 | 24.1416 | 62.4
Talwandi | JT - 834 | 7.5 | Submersible | 13.107 | 20.7708 | 17.1575 | 15.5658 | 13.107 | 20.7708 | 58.5
Talwandi | JT - 1060 | 7.5 | Submersible | 12.7752 | 19.0194 | 5.0835 | 46.8891 | 12.7752 | 19.0194 | 58.5
Talwandi | JT - 557 | 7.5 | Submersible | 13.6101 | 25.6118 | 8.3332 | 41.0357 | 13.6101 | 25.6118 | 62.4
Talwandi | JT - 379 | 12.5 | Submersible | 13.2571 | 21.5054 | 7.7316 | 36.1738 | 13.2571 | 21.5054 | 58.5
Talwandi | New Connection | 7.5 | Monoblock | 13.2644 | 18.3599 | 4.5586 | 52.4075 | 13.2644 | 18.3599 | 60
Talwandi | JT - 1019 | 7.5 | Monoblock | 14.4787 | 28.9762 | 7.6388 | 53.8783 | 14.4787 | 28.9762 | 64
Talwandi | JT - 767 | 12.5 | Submersible | 14.632 | 33.4076 | 12.7045 | 37.7452 | 14.632 | 33.4076 | 60
Talwandi | New Connection | 7.5 | Submersible | 13.1527 | 19.2555 | 7.5954 | 32.7104 | 13.1527 | 19.2555 | 58.5
Talwandi | JM - 956 | 7.5 | Submersible | 13.3265 | 17.2811 | 7.7801 | 29.0384 | 13.3265 | 17.2811 | 60
Talwandi | JT - 725 | 7.5 | Submersible | 13.669 | 22.0696 | 5.8798 | 50.3314 | 13.669 | 22.0696 | 62.4
Talwandi | JT - 662 | 7.5 | Submersible | 13.1836 | 20.2657 | 6.4237 | 40.8017 | 13.1836 | 20.2657 | 58.5
Talwandi | JT - 552 | 7.5 | Submersible | 13.393 | 19.8282 | 5.6005 | 46.5159 | 13.393 | 19.8282 | 58.5
Talwandi | New Connection | 7.5 | Submersible | 13.1043 | 18.315 | 6.5482 | 35.9557 | 13.1043 | 18.315 | 60
Talwandi | JT - 681 | 7.5 | Submersible | 14.2702 | 17.12 | 6.8654 | 34.909 | 14.2702 | 17.12 | 60
Talwandi | JT - 363 | 7.5 | Monoblock | 13.619 | 19.2308 | 5.1987 | 49.4214 | 13.619 | 19.2308 | 58.5
Talwandi | JT - 914 | 7.5 | Submersible | 13.2938 | 21.0723 | 7.1991 | 38.1726 | 13.2938 | 21.0723 | 58.5
Talwandi | JT - 219 | 7.5 | Submersible | 13.4329 | 18.8877 | 7.2748 | 34.2132 | 13.4329 | 18.8877 | 58.5
Talwandi | New Connection | 7.5 | Submersible | 13.8309 | 21.8553 | 6.9721 | 42.5316 | 13.8309 | 21.8553 | 60
Talwandi | JB - 174 | 7.5 | Submersible | 13.3987 | 16.9715 | 7.6326 | 29.2266 | 13.3987 | 16.9715 | 60
Talwandi | JT - 209 | 7.5 | Submersible | 13.6279 | 22.4215 | 7.4204 | 40.3957 | 13.6279 | 22.4215 | 60
Talwandi | JT - 518 | 7.5 | Submersible | 14.8384 | 16.9492 | 7.9139 | 31.1754 | 14.8384 | 16.9492 | 60
Talwandi | New Connection | 7.5 | Submersible | 15.1727 | 18.6741 | 6.5141 | 42.6693 | 15.1727 | 18.6741 | 58.5
Talwandi | JT - 766 | 7.5 | Submersible | 14.291 | 28.4001 | 6.5284 | 60.9884 | 14.291 | 28.4001 | 62.4
Talwandi | JT - 855 | 7.5 | Submersible | 13.1752 | 14.4485 | 7.2848 | 25.635 | 13.1752 | 14.4485 | 60
Talwandi | JT - 147 | 5 | Submersible | 14.5339 | 16.0256 | 5.7128 | 39.9963 | 14.5339 | 16.0256 | 60
Talwandi | JT - 337 | 5 | Submersible | 14.0985 | 26.5957 | 6.7828 | 54.2308 | 14.0985 | 26.5957 | 60
Talwandi | JT - 1083 | 7.5 | Submersible | 13.5257 | 19.6335 | 5.3407 | 48.7784 | 13.5257 | 19.6335 | 58.5
Talwandi | JM - 8 | 7.5 | Submersible | 13.9565 | 24.6373 | 6.9199 | 48.7462 | 13.9565 | 24.6373 | 62.4
Talwandi | G - 47 | 5 | Submersible | 14.1523 | 28.8092 | 9.0239 | 44.3235 | 14.1523 | 28.8092 | 60
Talwandi | New Connection | 7.5 | Submersible | 13.6074 | 22.2332 | 9.4134 | 31.5281 | 13.6074 | 22.2332 | 62.4
Talwandi | G -25 | 7.5 | Submersible | 14.9326 | 36.2027 | 15.3889 | 34.4618 | 14.9326 | 36.2027 | 60
Talwandi | JM - 596 | 5 | Submersible | 13.393 | 22.3491 | 5.8568 | 50.136 | 13.393 | 22.3491 | 62.4
Talwandi | G - 4 | 5 | Monoblock | 12.754 | 24.0513 | 7.0314 | 42.7965 | 12.754 | 24.0513 | 62.4
Talwandi | G - 62 | 5 | Submersible | 13.7849 | 24.57 | 8.1519 | 40.7587 | 13.7849 | 24.57 | 62.4
Talwandi | JM - 1078 | 7.5 | Submersible | 14.5027 | 34.1297 | 10.6567 | 45.5645 | 14.5027 | 34.1297 | 56.25
Talwandi | G - 138 | 5 | Submersible | 14.5717 | 35.5731 | 8.7795 | 57.9202 | 14.5717 | 35.5731 | 56.25
Talwandi | JB - 1050 | 7.5 | Submersible | 14.1713 | 24.5566 | 9.7342 | 35.071 | 14.1713 | 24.5566 | 62.4
Talwandi | JT - 768 | 7.5 | Submersible | 13.5963 | 21.2867 | 7.1863 | 39.5086 | 13.5963 | 21.2867 | 58.5
Talwandi | JT - 1009 | 7.5 | Submersible | 13.9826 | 25.9665 | 8.4912 | 41.9471 | 13.9826 | 25.9665 | 62.4
Talwandi | JT - 1059 | 7.5 | Submersible | 14.7074 | 12.0112 | 4.5195 | 38.3443 | 14.7074 | 12.0112 | 57
Talwandi | JT - 469 | 5 | Submersible | 13.8327 | 15.9801 | 6.5425 | 33.1444 | 13.8327 | 15.9801 | 60
Talwandi | JT - 543 |  | Submersible | 13.8752 | 16.1117 | 6.6357 | 33.0491 | 13.8752 | 16.1117 | 60
Talwandi | JT - 769 | 7.5 | Submersible | 13.5261 | 19.4974 | 6.3205 | 40.9328 | 13.5261 | 19.4974 | 58.5
Talwandi | JT - 441 | 5 | Submersible | 15.4981 | 20.1748 | 10.9351 | 28.0502 | 15.4981 | 20.1748 | 58.5
Talwandi | JT - 553 | 7.5 | Submersible | 13.8499 | 23.301 | 6.0465 | 52.3582 | 13.8499 | 23.301 | 62.4
Talwandi | JT - 392 | 7.5 | Submersible | 14.1054 | 24.321 | 8.416 | 39.988 | 14.1054 | 24.321 | 62.4
Talwandi | JM - 660 | 7.5 | Submersible | 14.0459 | 26.2467 | 10.3203 | 35.043 | 14.0459 | 26.2467 | 62.4
Talwandi | JM - 100 | 7.5 | Submersible | 14.2414 | 28.3465 | 11.4904 | 34.4654 | 14.2414 | 28.3465 | 62.4
Talwandi | JM - 19 | 7.5 | Submersible | 13.7328 | 21.9566 | 5.8399 | 50.6505 | 13.7328 | 21.9566 | 62.4
Talwandi | JM - 12 | 12.5 | Submersible | 13.4151 | 18.4049 | 6.2455 | 38.7822 | 13.4151 | 18.4049 | 60
Talwandi | JM - 564 | 5 | Submersible | 13.6146 | 21.2014 | 5.6261 | 50.3309 | 13.6146 | 21.2014 | 58.5
Talwandi | JM - 186 | 7.5 | Submersible | 14.3085 | 14.3426 | 5.3428 | 37.6809 | 14.3085 | 14.3426 | 60
Talwandi | JM - 632 | 7.5 | Submersible | 13.614 | 20.5761 | 7.0939 | 38.7373 | 13.614 | 20.5761 | 58.5
Talwandi | JM - 919 | 12.5 | Submersible | 13.3372 | 16.5138 | 6.4084 | 33.7157 | 13.3372 | 16.5138 | 60
Talwandi | JM - 295 | 7.5 | Submersible | 13.9143 | 25.1046 | 6.3659 | 53.8302 | 13.9143 | 25.1046 | 62.4
Talwandi | JT - 338 | 7.5 | Submersible | 13.6851 | 22.1893 | 7.072 | 42.123 | 13.6851 | 22.1893 | 62.4
Talwandi | JT - 559 | 7.5 | Submersible | 13.6615 | 21.097 | 7.7306 | 36.5745 | 13.6615 | 21.097 | 58.5
Talwandi | New Connection | 5 | Monoblock | 13.4681 | 17.8042 | 5.0737 | 46.3632 | 13.4681 | 17.8042 | 60
Talwandi | JT - 161 | 7.5 | Submersible | 16.3676 | 23.1036 | 5.7832 | 64.1457 | 16.3676 | 23.1036 | 62.4
Talwandi | JT - 1041 | 7.5 | Submersible | 14.0601 | 26.004 | 8.4253 | 42.5709 | 14.0601 | 26.004 | 62.4
Talwandi | JT - 641 | 7.5 | Submersible | 13.5134 | 19.9071 | 6.6855 | 39.4736 | 13.5134 | 19.9071 | 58.5
Talwandi | JT - 166 | 6 | Submersible | 13.6017 | 21.1119 | 7.6173 | 36.9818 | 13.6017 | 21.1119 | 58.5
Talwandi | JT - 407 | 7.5 | Submersible | 14.6853 | 16.5017 | 6.8948 | 34.4792 | 14.6853 | 16.5017 | 60
Talwandi | JT - 9 | 5 | Submersible | 13.3571 | 17.508 | 4.8626 | 47.1793 | 13.3571 | 17.508 | 60
Talwandi | JT - 06 | 7.5 | Submersible | 13.4454 | 18.6451 | 7.8565 | 31.3026 | 13.4454 | 18.6451 | 58.5
Talwandi | JT - 1075 | 7.5 | Submersible | 13.4352 | 18.4275 | 7.4201 | 32.732 | 13.4352 | 18.4275 | 58.5
Talwandi | JT - 910 | 5 | Submersible | 14.038 | 13.5338 | 5.8393 | 31.9179 | 14.038 | 13.5338 | 56.25
Talwandi | JT - 559 | 7.5 | Submersible | 13.7847 | 22.4831 | 7.8038 | 38.96 | 13.7847 | 22.4831 | 62.4
Talwandi | S1 - 127 | 7.5 | Submersible | 13.8467 | 24.2326 | 8.4569 | 38.9227 | 13.8467 | 24.2326 | 62.4
Talwandi | JM - 689 | 7.5 | Submersible | 16.4369 | 24.2915 | 10.1147 | 38.7248 | 16.4369 | 24.2915 | 62.4
Talwandi | G - 237 | 7.5 | Submersible | 14.9662 | 18.1525 | 7.9857 | 33.3736 | 14.9662 | 18.1525 | 58.5
Talwandi | JM - 103 | 7.5 | Submersible | 14.0451 | 29.7422 | 8.3196 | 49.2568 | 14.0451 | 29.7422 | 60
Talwandi | G - 184 | 7.5 | Submersible | 13.9934 | 29.1262 | 11.1783 | 35.7685 | 13.9934 | 29.1262 | 60
Talwandi | JM - 576 | 7.5 | Submersible | 14.1839 | 30.9278 | 9.9232 | 43.367 | 14.1839 | 30.9278 | 60
Talwandi | JM - 100 | 7.5 | Submersible | 13.2207 | 20.723 | 7.1448 | 37.6174 | 13.2207 | 20.723 | 58.5
Talwandi | JM - 71 | 7.5 | Submersible | 14.6647 | 34.4037 | 10.202 | 48.513 | 14.6647 | 34.4037 | 60
Talwandi | JM - 136 | 5 | Submersible | 16.9971 | 27.1575 | 7.8568 | 57.6355 | 16.9971 | 27.1575 | 62.4
Talwandi | JM - 667 | 5 | Submersible | 15.6744 | 21.797 | 8.4559 | 39.637 | 15.6744 | 21.797 | 58.5
Talwandi | JM - 909 | 6 | Submersible | 16.3643 | 24.1611 | 7.8811 | 49.2147 | 16.3643 | 24.1611 | 62.4
Talwandi | JM - 1090 | 6 | Submersible | 13.6231 | 22.0805 | 7.9896 | 36.9339 | 13.6231 | 22.0805 | 62.4
Talwandi | G - 185 | 3 | Submersible | 14.8754 | 18.2556 | 8.0992 | 32.8921 | 14.8754 | 18.2556 | 58.5
Talwandi | JM - 1108 | 5 | Submersible | 13.5139 | 20.3069 | 7.0044 | 38.4344 | 13.5139 | 20.3069 | 58.5
Talwandi | JM - 195 | 5 | Submersible | 16.0234 | 22.2497 | 6.0277 | 58.0223 | 16.0234 | 22.2497 | 62.4
Talwandi | JM - 400 | 5 | Submersible | 17.4789 | 22.0913 | 6.9392 | 54.5881 | 17.4789 | 22.0913 | 62.4
Talwandi | JM - 403 | 7.5 | Submersible | 14.4017 | 32.491 | 9.9585 | 46.0948 | 14.4017 | 32.491 | 64
Talwandi | JT - 741 | 7.5 | Submersible | 13.7324 | 26.1552 | 10.0079 | 35.207 | 13.7324 | 26.1552 | 62.4
Talwandi | JT - 448 | 10 | Submersible | 13.9077 | 23.6035 | 6.9285 | 46.4792 | 13.9077 | 23.6035 | 60
Talwandi | JT - 1052 | 5 | Monoblock | 13.1274 | 16.3088 | 5.3055 | 39.586 | 13.1274 | 16.3088 | 60
Talwandi | JT - 1180 | 7.5 | Submersible | 14.2248 | 20.9692 | 8.2674 | 35.3939 | 14.2248 | 20.9692 | 58.5
Talwandi | JT - 1070 | 7.5 | Submersible | 15.1804 | 19.4637 | 6.1405 | 47.2034 | 15.1804 | 19.4637 | 58.5
Talwandi | JT - 624 | 7.5 | Submersible | 13.5827 | 19.6207 | 5.09 | 51.363 | 13.5827 | 19.6207 | 58.5
Talwandi | JT - 746 | 7.5 | Submersible | 13.6538 | 22.3104 | 5.4612 | 54.7196 | 13.6538 | 22.3104 | 60.84
Talwandi | JB - 872 | 7.5 | Submersible | 14.4676 | 14.2631 | 6.5948 | 30.6959 | 14.4676 | 14.2631 | 56.25
Talwandi | JT - 440 | 7.5 | Submersible | 13.3762 | 18.4502 | 5.8889 | 41.1118 | 13.3762 | 18.4502 | 58.5
Talwandi | New Connection | 7.5 | Submersible | 13.4937 | 20.4267 | 5.178 | 52.2201 | 13.4937 | 20.4267 | 58.5
Talwandi | JT - 724 | 12.5 | Submersible | 14.4974 | 30.7692 | 9.3211 | 46.9472 | 14.4974 | 30.7692 | 64
Talwandi | JB - 799 | 7.5 | Submersible | 14.3623 | 26.1704 | 8.9339 | 41.2726 | 14.3623 | 26.1704 | 62.4
Talwandi | JT - 941 | 7.5 | Submersible | 13.3886 | 18 | 5.0803 | 46.5354 | 13.3886 | 18 | 58.5
Talwandi | JT - 676 | 5 | Submersible | 14.7703 | 17.2348 | 6.9849 | 35.7525 | 14.7703 | 17.2348 | 58.5
Talwandi | JT - 1018 | 7.5 | Submersible | 13.7846 | 23.5911 | 5.4485 | 58.5508 | 13.7846 | 23.5911 | 62.4
Talwandi | JB - 563 | 5 | Submersible | 14.7294 | 32.5615 | 8.3386 | 56.4241 | 14.7294 | 32.5615 | 64
Talwandi | JT - 590 | 7.5 | Submersible | 13.3123 | 16.2955 | 6.5152 | 32.6637 | 13.3123 | 16.2955 | 58.5
Talwandi | JT - 226 | 7.5 | Submersible | 13.8596 | 23.4926 | 9.0927 | 35.1283 | 13.8596 | 23.4926 | 62.4
Talwandi | JM - 547 | 7.5 | Submersible | 13.2735 | 15.7729 | 6.477 | 31.7099 | 13.2735 | 15.7729 | 60
Talwandi | JM - 90 | 7.5 | Submersible | 14.9671 | 35.0467 | 10.6937 | 48.12 | 14.9671 | 35.0467 | 64
Talwandi | JM - 324 | 5 | Submersible | 14.8373 | 17.301 | 6.0004 | 41.9675 | 14.8373 | 17.301 | 58.5
Talwandi | JM - 997 | 7.5 | Submersible | 13.4318 | 18.5147 | 6.5774 | 37.0909 | 13.4318 | 18.5147 | 58.5